## Index
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
INDEX
Steam Pipe Size | Steam Pipe Sizing
Sheet 1 | Water Flow Calculator
Sheet 2 | Condensate & Flash Steam Saving
Sheet 3 | De-superheating Station (PRDS)
Sheet 4 | Saturated Steam Table
Sheet 5 | Boiler Efficiency Calculation
Sheet 6 | Blow down Saving Calculation
Sheet 7 | Steam Requirement for Process Heating
Sheet 8 | Steam required for Evaporation
Sheet 9 | Feed Tank Temp.
Sheet 10 | Tank Dimensions & weight
Sheet 11 | Heating & Cooling System
Sheet 12 | Safety Valve Orifice
Sheet 13 | Weight Calculator for Pipe, Plate, Tube, C & I section and Angle
Sheet 14 | PIPE WALL THICKNESS CALCULATOR ASME B31.3
Sheet 15 | F & A Calculator for Boiler Capacity
Sheet 16 | Steam Saving in PRS
Sheet 17 | Superheated Steam Cal
Sheet 18 | PIPE WALL THICKNESS CALCULATOR ASME B31.3 FOR P11 / P22

## Steam Pipe Size
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
ONLY FOR SATURATED STEAM PIPE SIZE CALCULATOR
Calculation of Pipe Diameter from Steam Flow |  |  | Pipe Steam Flow Capacity from Diameter |  |  | INDEX
Steam Flow Rate | 8000 | kg/hr | Steam Pressure | 3.45 | bar (g)
Steam Pressure | 6 | bar (g) | Pipe Internal Dia. | 100 | mm
Steam Specific Volume | 0.273 | m3/kg | Steam Specific Volume | #N/A | m3/kg
Steam Flow Rate | 2184 | m3/hr |  | 0.1 | mtr
| 0.60667 | m³/sec
Velocity | 25 | m/s | Velocity | 25 | m/s
Diameter of Pipe | 0.17582 | mtr | Flow Capacity of pipe | 706.5 | m³/hr
Diameter of Pipe | 175.8208 | mm | Flow Capacity of pipe | #N/A | kg/hr
Input to be provided
Result

## Sheet1
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
VOLUMETRIC FLOW CALCULATOR
Calculation of Pipe Diameter from Flow |  |  | Pipe Volumetric Flow Capacity from Diameter |  |  | INDEX
Flow | 0.18 | m³/hr | Diameter | 100 | mm
| 5e-05 | m³/sec |  | 0.1 | mtr
Velocity | 1.5 | m/s | Velocity | 1 | m/s
Diameter of Pipe | 0.0065164 | mtr | Flow Capacity of pipe | 0.00785 | m³/sec
| 6.5164 | mm |  | 28.26 | m³/hr
Input to be provided
Result

## Sheet2
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
Condensate & Flash Steam Saving Calculator
CUSTOMER NAME |  |  |  |  | Fuel | GCV
Boiler Fuel Used | Gas |  | INDEX | Input Fields | Wood | 3500
GCV of Fuel | 9600 | Kcal/kg |  | Result | Briquette | 4000
Price of Fuel | 8 | Rs./kg |  |  | Coal | 5000
Boiler Efficiency | 90% |  |  |  | FO | 10200
Operational Hours per Day | 24 | hrs/day |  |  | Diesel | 10500
Operational Days per Year | 250 | Days/year |  |  | Gas | 9800
Qty of Condensate | 1000 | kg/hr |  |  | Petcoke | 7500
Condensate Pressure | 3.5 | bar (g) |  |  | Rice Husk | 3000
Condensate Temp | 148 | Deg C
Flash Steam Pressure | 1 | bar (g)
Flash Steam Temp | 120.2 | Deg C
Latent heat @ Flash steam pressure | 525.79 | Kcal/kg
Total heat @ Flash steam pressure | 646.57 | Kcal/kg
Diff. Temp | 27.8 | Deg C
% Flash Steam | 5.287%
Flash Steam | 52.8728 | kg/hr
| 34185.9792 | kCal/hr
Balance Condensate After Flash Steam Gen. | 947.1272 | kg/hr
Equivalent Fuel Saving | 3.9567 | kg/hr
Equivalent Saving in Rs. | 31.6537 | Rs./hr
Saving due to flash steam recovery | 189922.1066 | Rs. Per year
Total Heat Recovered in Condensate | 94712.718 | Kcal
Equivalent Fuel Saving | 10.9621 | kg/hr
Equivalent Saving in Rs. | 87.697 | Rs. Per hour
Saving Due to Condensate Recovery | 526181.7667 | Rs. Per Year
Saving Total (Flash + Condensate) | 716103.8733 | Rs per Year

## Copy of Sheet2
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
Condensate & Flash Steam Saving Calculator
CUSTOMER NAME | Mangalm Organics Pvt Ltd |  |  |  | Fuel | GCV
Boiler Fuel Used | Coal |  | INDEX | Input Fields | Wood | 3500
GCV of Fuel | 5700 | Kcal/kg |  | Result | Briquette | 4000
Price of Fuel | 8 | Rs./kg |  |  | Coal | 5000
Boiler Efficiency | 80% |  |  |  | FO | 10200
Operational Hours per Day | 24 | hrs/day |  |  | Diesel | 10500
Operational Days per Year | 360 | Days/year |  |  | Gas | 9800
Qty of Condensate | 800 | kg/hr |  |  | Petcoke | 7500
Condensate Pressure | 0 | bar (g) |  |  | Rice Husk | 3000
Condensate Temp | 85 | Deg C
Total Heat Recovered in Condensate | 68000 | Kcal
Equivalent Fuel Saving | 14.9123 | kg/hr
Equivalent Saving in Rs. | 119.2982 | Rs. Per hour
Saving Due to Condensate Recovery | 1030736.842 | Rs. Per Year

## Sheet3
x | VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
PRDS CALCULATOR
Media: Superheated Steam | INQ2025568 | TAG NO. | INDEX |  |  | INLET PRDS SIZE |  |  | Calculation for steam at inlet of PRV |  |  |  | Calculation at outlet of de-superheater |  |  |  | Calculation for steam at outlet of PRV
Superheated Steam Flow rate | 8000 | kg/hr | PRDS Inlet |  | UNIT | Flow | 1418.8144 | m³/hr | Steam Pressure | 11 | bar (abs) | 647.14 | Steam Pressure | 7 | bar (abs) | 647.14 | Steam Pressure | 7 | bar (abs) | 647.14
Steam Inlet Pressure | 10 | bar (g) | Superheated Steam Flow rate | 8000 | kg/hr |  | 0.39412 | m³/sec | Steam Temperature | 184.123 | celsius | 220.64 | Steam Temperature | 165 | celsius | 220.64 | Steam Temperature | 221 | celsius | 220.64
Steam Inlet Temp. | 184.123 | Deg C | Operating Pressure | 10 | Bar (g) | Diameter of Pipe | 0.22869 | mtr | Steam Flow rate | 43000 | kg/hr |  | Steam Flow rate | 43000 | kg/hr |  | Steam temp | 494.14 | kelvin
Steam Outlet Pressure | 6 | bar (g) | Operating Temperature | 184.123 | Deg C |  | 228.6868 | mm | Steam Velocity | 35 | m/sec |  | Steam Velocity | 35 | m/sec |  | Temp reduction | 0.76358
Required Outlet Temp. (Saturation temp.@ outlet pressure / as per customer requirement) | 165 | Deg C | Line Size | 150NB | [12 empty] | Pressure reduction | 0.031726
Water temp. (Assume/ given by customer) |  | Deg C | MOC TABLE | MOC | CLASS | OUTLET PRDS SIZE |  |  | Steam temp | 457.263 | kelvin |  | Steam temp | 438.14 | kelvin |  | Zpbe_H2O | 0.96609
Water pressure (Assume/ given by customer) |  | bar (g) | Flange/Forged Products | A 105 | FL 150 | Flow | 2519.9699 | m³/hr | Temp reduction | 0.70659 |  |  | Temp reduction | 0.67704
Steam Outlet Temp. (Superheated temp.@ outlet pressure) | 221 | Deg C | Valve/Srainer/Casted Product | A216 WCB | FL 150 |  | 0.69999 | m³/sec | Pressure reduction | 0.049855 |  |  | Pressure reduction | 0.031726 |  |  | Enthalpy | 2888.6481 | KJ/Kg
Total heat @Inlet Superheated Pre. & Temp. | 662.9525 | Kcal/kg | Pipe/Bend/Reducers | A106 Grade B | SCHEDULE 40 | Diameter of Pipe | 0.21534 | mtr | Zpbe_H2O | 0.92369 |  |  | Zpbe_H2O | 0.94316 |  |  | Enthalpy(at outlet of valve) | 690.4035 | Kcal/Kg
Total heat @Outlet Superheated Pre. & Temp. | 690.4035 | Kcal/kg |  |  |  |  | 215.3386 | mm | [8 empty] | Density | 3.1746 | Kg/m3
Total heat @Required Pre. & Temp. at Outlet of De-Superheater | 658.3961 | Kcal/kg | PRS Outlet |  | UNIT |  |  |  | Enthalpy | 2773.7932 | KJ/Kg |  | Enthalpy | 2754.7294 | KJ/Kg |  | Specific volume | 0.315 | m3/kg
Sp. Volume @Inlet Superheated Pre. & Temp. | 0.17735 | m3/kg | Operating Pressure | 6 | Bar (g) | OUTLET Desuperheater SIZE |  |  | Enthalpy | 662.9525 | Kcal/Kg |  | Enthalpy | 658.3961 | Kcal/Kg
Sp. Volume @Outlet Superheated Pre. & Temp. | 0.315 | m3/kg | Operating Temperature | 221 | Deg C | Flow | 2196.4598 | m³/hr | Density | 5.6385 | Kg/m3 |  | Density | 3.6674 | Kg/m3
Sp. Volume @Outlet of De-Superheater Pr. & Temp. | 0.27267 | m3/kg | Required Outlet Temp. (Saturation temp.@ outlet pressure / as per customer requirement) | 165 | Deg C |  | 0.61013 | m³/sec | Specific volume | 0.17735 | m3/kg |  | Specific volume | 0.27267 | m3/kg
|  |  | Line Size | 200NB |  | Diameter of Pipe | 0.21288 | mtr | Diameter of pipe | 0.2776 | m |  | Diameter of pipe | 0.34421 | m
Available extra heat in per kg of Steam | 4.5563 | Kcal/kg | MOC TABLE | MOC | CLASS |  | 212.8842 | mm | Diameter of Pipe | 277.6015 | mm |  | Diameter of Pipe | 344.2097 | mm
Available extra heat in total Steam | 36450.6943 | Kcal/hr | Flange/Forged Products | A 105 | FL 150
Heat Gain by Water | 658.3961 | Kcal/kg | Valve/Srainer/Casted Product | A216 WCB | FL 150 | WATER INLET TO Desuperheater SIZE
|  |  | Pipe/Bend/Reducers | A106 Grade B | SCHEDULE 40 | Flow | 0.055363 | m³/hr
Required Water Quantity for Desuperheating the Steam | 55.3629 | Kg/hr |  |  |  |  | 1.5379e-05 | m³/sec
STEAM VELOCITY AT INLET | 9.6 | m/s | DE-SUPERHEATER ASSEMBLY |  | UNIT | Diameter of Pipe | 0.0036139 | mtr
PRDS INLET CALCULATED LINE SIZE | 228.6868 | mm | Operating Pressure |  | Bar (g) |  | 3.6139 | mm
STEAM VELOCITY AT PRS OUTLET | 19.23 | m/s | Operating Temperature |  | Deg C
CALCULATED LINE SIZE AT THE OUTLET OF PRS | 215.3386 | mm | Required Water Quantity for Desuperheating the Steam | 55.3629 | Kg/hr
STEAM VELOCITY AT DESUPERHEATER OUTLET | 17.15 | m/s | Line Size | 15NB
CALCULATED LINE SIZE AT THE OUTLET OF DESUPERHEATER | 212.8842 | mm | MOC TABLE | MOC | CLASS
WATER INJECTION VELOCITY AT DESUPERHEATER | 1.5 | m/s | Flange/Forged Products | A 105 | FL 150
CALCULATED LINE SIZE FOR WATER | 3.6139 | mm | Valve/Srainer/Casted Product | A216 WCB | FL 150
|  |  | Pipe/Bend/Reducers | A106 Grade B | SCHEDULE 40
Input Fields
Result
Please refer the below link for Superheated Steam Table
https://www.tlv.com/global/TI/calculator/superheated-steam-table.html

## Sheet60 (hidden)
x | VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
PRDS CALCULATOR
| INQ2025130 | PROCIENT
Media: Superheated Steam | PRDS | TAG NO. | INDEX |  |  | INLET PRDS SIZE |  |  | Calculation for steam at inlet of PRV |  |  |  | Calculation at outlet of de-superheater |  |  |  | Calculation for steam at outlet of PRV
Superheated Steam Flow rate | 54353 | kg/hr | PRDS Inlet |  | UNIT | Flow | 7341.4876 | m³/hr | Steam Pressure | 19 | bar (abs) | 647.14 | Steam Pressure | 5.1 | bar (abs) | 647.14 | Steam Pressure | 5.1 | bar (abs) | 647.14
Steam Inlet Pressure | 18 | bar (g) | Operating Pressure | 18 | Bar (g) |  | 2.0393 | m³/sec | Steam Temperature | 310 | celsius | 220.64 | Steam Temperature | 152.682 | celsius | 220.64 | Steam Temperature | 290 | celsius | 220.64
Steam Inlet Temp. | 310 | Deg C | Operating Temperature | 310 | Deg C | Diameter of Pipe | 0.2601 | mtr | Steam Flow rate | 43000 | kg/hr |  | Steam Flow rate | 43000 | kg/hr |  | Steam temp | 563.14 | kelvin
Steam Outlet Pressure | 4.1 | bar (g) | Line Size | 250 | NB |  | 260.1 | mm | Steam Velocity | 35 | m/sec |  | Steam Velocity | 35 | m/sec |  | Temp reduction | 0.8702
Required Outlet Temp. (Saturation temp.@ outlet pressure / as per customer requirement) | 152.682 | Deg C | MOC TABLE | MOC | CLASS | [11 empty] | Pressure reduction | 0.023115
Water temp. (Assume/ given by customer) | 50 | Deg C | Flange/Forged Products | A 105 | FL 300 | OUTLET PRDS SIZE |  |  | Steam temp | 583.14 | kelvin |  | Steam temp | 425.822 | kelvin |  | Zpbe_H2O | 0.98584
Water pressure (Assume/ given by customer) | 6.1 | bar (g) | Valve/Srainer/Casted Product | A216 WCB | FL 300 | Flow | 27328.329 | m³/hr | Temp reduction | 0.9011 |  |  | Temp reduction | 0.65801
Steam Outlet Temp. (Superheated temp.@ outlet pressure) | 290 | Deg C | Pipe/Bend/Reducers | A106 Grade B | SCHEDULE 20 |  | 7.5912 | m³/sec | Pressure reduction | 0.086113 |  |  | Pressure reduction | 0.023115 |  |  | Enthalpy | 3051.0393 | KJ/Kg
Total heat @Inlet Superheated Pre. & Temp. | 729.4421 | Kcal/kg |  |  |  | Diameter of Pipe | 0.54632 | mtr | Zpbe_H2O | 0.9528 |  |  | Zpbe_H2O | 0.95391 |  |  | Enthalpy(at outlet of valve) | 729.2159 | Kcal/Kg
Total heat @Outlet Superheated Pre. & Temp. | 729.2159 | Kcal/kg | PRS Outlet |  | UNIT |  | 546.3211 | mm | [8 empty] | Density | 1.9889 | Kg/m3
Total heat @Required Pre. & Temp. at Outlet of De-Superheater | 654.8833 | Kcal/kg | Operating Pressure | 4.1 | Bar (g) |  |  |  | Enthalpy | 3051.9856 | KJ/Kg |  | Enthalpy | 2740.0317 | KJ/Kg |  | Specific volume | 0.50279 | m3/kg
Sp. Volume @Inlet Superheated Pre. & Temp. | 0.13507 | m3/kg | Operating Temperature | 290 | Deg C | OUTLET Desuperheater SIZE |  |  | Enthalpy | 729.4421 | Kcal/Kg |  | Enthalpy | 654.8833 | Kcal/Kg
Sp. Volume @Outlet Superheated Pre. & Temp. | 0.50279 | m3/kg | Line Size | 550 | NB | Flow | 22459.9012 | m³/hr | Density | 7.4035 | Kg/m3 |  | Density | 2.7183 | Kg/m3
Sp. Volume @Outlet of De-Superheater Pr. & Temp. | 0.36788 | m3/kg | MOC TABLE | MOC | CLASS |  | 6.2389 | m³/sec | Specific volume | 0.13507 | m3/kg |  | Specific volume | 0.36788 | m3/kg
|  |  | Flange/Forged Products | A 105 | FL 150 | Diameter of Pipe | 0.54661 | mtr | Diameter of pipe | 0.24226 | m |  | Diameter of pipe | 0.39981 | m
Available extra heat in per kg of Steam | 74.5588 | Kcal/kg | Valve/Srainer/Casted Product | A216 WCB | FL 150 |  | 546.6093 | mm | Diameter of Pipe | 242.2614 | mm |  | Diameter of Pipe | 399.8119 | mm
Available extra heat in total Steam | 4052492.162 | Kcal/hr | Pipe/Bend/Reducers | A106 Grade B | SCHEDULE 10
Heat Gain by Water | 604.8833 | Kcal/kg |  |  |  | WATER INLET TO Desuperheater SIZE
|  |  | DE-SUPERHEATER ASSEMBLY |  | UNIT | Flow | 6.6996 | m³/hr
Required Water Quantity for Desuperheating the Steam | 6699.6265 | Kg/hr | Operating Pressure | 6.1 | Bar (g) |  | 0.001861 | m³/sec
STEAM VELOCITY AT INLET | 38.4 | m/s | Operating Temperature | 50 | Deg C | Diameter of Pipe | 0.040435 | mtr
PRDS INLET CALCULATED LINE SIZE | 260.1 | mm | Line Size | 40 | NB |  | 40.4348 | mm
STEAM VELOCITY AT PRS OUTLET | 32.4 | m/s | MOC TABLE | MOC | CLASS
CALCULATED LINE SIZE AT THE OUTLET OF PRS | 546.3211 | mm | Flange/Forged Products | A 105 | FL 300
STEAM VELOCITY AT DESUPERHEATER OUTLET | 26.6 | m/s | Valve/Srainer/Casted Product | A216 WCB | FL 300
CALCULATED LINE SIZE AT THE OUTLET OF DESUPERHEATER | 546.6093 | mm | Pipe/Bend/Reducers | A106 Grade B | SCHEDULE 40
WATER INJECTION VELOCITY AT DESUPERHEATER | 1.45 | m/s
CALCULATED LINE SIZE FOR WATER | 40.4348 | mm
Input Fields
Result
Please refer the below link for Superheated Steam Table
https://www.tlv.com/global/TI/calculator/superheated-steam-table.html

## Sheet58 (hidden)
x | VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
PRDS CALCULATOR
INQ2025046
Media: Superheated Steam | PRDS 2 | TAG NO. | INDEX |  |  | INLET PRDS SIZE |  |  | Calculation for steam at inlet of PRV |  |  |  | Calculation at outlet of de-superheater |  |  |  | Calculation for steam at outlet of PRV
Superheated Steam Flow rate | 25000 | kg/hr | PRDS Inlet |  | UNIT | Flow | 27657.7689 | m³/hr | Steam Pressure | 2.8 | bar (abs) | 647.14 | Steam Pressure | 2.5 | bar (abs) | 647.14 | Steam Pressure | 2.5 | bar (abs) | 647.14
Steam Inlet Pressure | 1.8 | bar (g) | Operating Pressure | 16 | Bar (g) |  | 7.6827 | m³/sec | Steam Temperature | 400 | celsius | 220.64 | Steam Temperature | 150 | celsius | 220.64 | Steam Temperature | 399 | celsius | 220.64
Steam Inlet Temp. | 400 | Deg C | Operating Temperature | 400 | Deg C | Diameter of Pipe | #DIV/0! | mtr | Steam Flow rate | 43000 | kg/hr |  | Steam Flow rate | 43000 | kg/hr |  | Steam temp | 672.14 | kelvin
Steam Outlet Pressure | 1.5 | bar (g) | Line Size |  | NB |  | #DIV/0! | mm | Steam Velocity | 35 | m/sec |  | Steam Velocity | 35 | m/sec |  | Temp reduction | 1.0386
Required Outlet Temp. (Saturation temp.@ outlet pressure / as per customer requirement) | 150 | Deg C | MOC TABLE | MOC | CLASS | [11 empty] | Pressure reduction | 0.011331
Water temp. (Assume/ given by customer) | 125 | Deg C | Flange/Forged Products |  |  | OUTLET PRDS SIZE |  |  | Steam temp | 673.14 | kelvin |  | Steam temp | 423.14 | kelvin |  | Zpbe_H2O | 0.99668
Water pressure (Assume/ given by customer) | 135 | bar (g) | Valve/Srainer/Casted Product |  |  | Flow | 30942.3848 | m³/hr | Temp reduction | 1.0402 |  |  | Temp reduction | 0.65386
Steam Outlet Temp. (Superheated temp.@ outlet pressure) | 399 | Deg C | Pipe/Bend/Reducers |  |  |  | 8.5951 | m³/sec | Pressure reduction | 0.01269 |  |  | Pressure reduction | 0.011331 |  |  | Enthalpy | 3290.5958 | KJ/Kg
Total heat @Inlet Superheated Pre. & Temp. | 786.842 | Kcal/kg |  |  |  | Diameter of Pipe | 0.5245 | mtr | Zpbe_H2O | 0.9963 |  |  | Zpbe_H2O | 0.97733 |  |  | Enthalpy(at outlet of valve) | 786.4713 | Kcal/Kg
Total heat @Outlet Superheated Pre. & Temp. | 786.4713 | Kcal/kg | PRS Outlet |  | UNIT |  | 524.5046 | mm | [8 empty] | Density | 0.80795 | Kg/m3
Total heat @Required Pre. & Temp. at Outlet of De-Superheater | 658.5517 | Kcal/kg | Operating Pressure | 1.5 | Bar (g) |  |  |  | Enthalpy | 3292.1469 | KJ/Kg |  | Enthalpy | 2755.3805 | KJ/Kg |  | Specific volume | 1.2377 | m3/kg
Sp. Volume @Inlet Superheated Pre. & Temp. | 1.1063 | m3/kg | Operating Temperature | 399 | Deg C | OUTLET Desuperheater SIZE |  |  | Enthalpy | 786.842 | Kcal/Kg |  | Enthalpy | 658.5517 | Kcal/Kg
Sp. Volume @Outlet Superheated Pre. & Temp. | 1.2377 | m3/kg | Line Size | 500 | NB | Flow | 23694.1739 | m³/hr | Density | 0.90391 | Kg/m3 |  | Density | 1.3088 | Kg/m3
Sp. Volume @Outlet of De-Superheater Pr. & Temp. | 0.76405 | m3/kg | MOC TABLE | MOC | CLASS |  | 6.5817 | m³/sec | Specific volume | 1.1063 | m3/kg |  | Specific volume | 0.76405 | m3/kg
|  |  | Flange/Forged Products | A 105 | FL 150 | Diameter of Pipe | 0.52517 | mtr | Diameter of pipe | 0.69333 | m |  | Diameter of pipe | 0.57619 | m
Available extra heat in per kg of Steam | 128.2902 | Kcal/kg | Valve/Srainer/Casted Product | A216 WCB | FL 150 |  | 525.1676 | mm | Diameter of Pipe | 693.3341 | mm |  | Diameter of Pipe | 576.1903 | mm
Available extra heat in total Steam | 3207256.248 | Kcal/hr | Pipe/Bend/Reducers | A106 Grade B | SCHEDULE 10
Heat Gain by Water | 533.5517 | Kcal/kg |  |  |  | WATER INLET TO Desuperheater SIZE
|  |  | DE-SUPERHEATER ASSEMBLY |  | UNIT | Flow | 6.0111 | m³/hr
Required Water Quantity for Desuperheating the Steam | 6011.1438 | Kg/hr | Operating Pressure | 135 | Bar (g) |  | 0.0016698 | m³/sec
STEAM VELOCITY AT INLET |  | m/s | Operating Temperature | 125 | Deg C | Diameter of Pipe | 0.037657 | mtr
PRDS INLET CALCULATED LINE SIZE | #DIV/0! | mm | Line Size | 40 | NB |  | 37.6571 | mm
STEAM VELOCITY AT PRS OUTLET | 39.8 | m/s | MOC TABLE | MOC | CLASS
CALCULATED LINE SIZE AT THE OUTLET OF PRS | 524.5046 | mm | Flange/Forged Products | A 105 | FL 900
STEAM VELOCITY AT DESUPERHEATER OUTLET | 30.4 | m/s | Valve/Srainer/Casted Product | A216 WCB | FL 900
CALCULATED LINE SIZE AT THE OUTLET OF DESUPERHEATER | 525.1676 | mm | Pipe/Bend/Reducers | A106 Grade B | SCHEDULE 160
WATER INJECTION VELOCITY AT DESUPERHEATER | 1.5 | m/s
CALCULATED LINE SIZE FOR WATER | 37.6571 | mm
Input Fields
Result
Please refer the below link for Superheated Steam Table
https://www.tlv.com/global/TI/calculator/superheated-steam-table.html

## Copy of Sheet3 (hidden)
x | VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
PRDS CALCULATOR
INQ2024-475
Media: Superheated Steam | PRDS--064 | TAG NO. | INDEX |  |  | INLET PRDS SIZE |  |  | Calculation for steam at inlet of PRV |  |  |  | Calculation at outlet of de-superheater |  |  |  | Calculation for steam at outlet of PRV
Superheated Steam Flow rate | 17000 | kg/hr | PRDS Inlet |  | UNIT | Flow | 1272.9669 | m³/hr | Steam Pressure | 46 | bar (abs) | 647.14 | Steam Pressure | 9 | bar (abs) | 647.14 | Steam Pressure | 9 | bar (abs) | 647.14
Steam Inlet Pressure | 45 | bar (g) | Operating Pressure | 45 | Bar (g) |  | 0.3536 | m³/sec | Steam Temperature | 500 | celsius | 220.64 | Steam Temperature | 185 | celsius | 220.64 | Steam Temperature | 415 | celsius | 220.64
Steam Inlet Temp. | 500 | Deg C | Operating Temperature | 500 | Deg C | Diameter of Pipe | 0.12684 | mtr | Steam Flow rate | 43000 | kg/hr |  | Steam Flow rate | 43000 | kg/hr |  | Steam temp | 688.14 | kelvin
Steam Outlet Pressure | 8 | bar (g) | Line Size | 200 | NB |  | 126.8363 | mm | Steam Velocity | 35 | m/sec |  | Steam Velocity | 35 | m/sec |  | Temp reduction | 1.0634
Required Outlet Temp. (Saturation temp.@ outlet pressure / as per customer requirement) | 185 | Deg C | MOC TABLE | MOC | CLASS | [11 empty] | Pressure reduction | 0.04079
Water temp. (Assume/ given by customer) | 105 | Deg C | Flange/Forged Products | A182 Gr. F22 | FL 600 | OUTLET PRDS SIZE |  |  | Steam temp | 773.14 | kelvin |  | Steam temp | 458.14 | kelvin |  | Zpbe_H2O | 0.98907
Water pressure (Assume/ given by customer) | 10 | bar (g) | Valve/Srainer/Casted Product | ASTM A217 WC9 | FL 600 | Flow | 5938.124 | m³/hr | Temp reduction | 1.1947 |  |  | Temp reduction | 0.70795
Steam Outlet Temp. (Superheated temp.@ outlet pressure) | 415 | Deg C | Pipe/Bend/Reducers | A182 Gr. P22 | SCHEDULE 40 |  | 1.6495 | m³/sec | Pressure reduction | 0.20848 |  |  | Pressure reduction | 0.04079 |  |  | Enthalpy | 3312.9581 | KJ/Kg
Total heat @Inlet Superheated Pre. & Temp. | 824.3101 | Kcal/kg |  |  |  | Diameter of Pipe | 0.29902 | mtr | Zpbe_H2O | 0.96456 |  |  | Zpbe_H2O | 0.93893 |  |  | Enthalpy(at outlet of valve) | 791.816 | Kcal/Kg
Total heat @Outlet Superheated Pre. & Temp. | 791.816 | Kcal/kg | PRS Outlet |  | UNIT |  | 299.023 | mm | [8 empty] | Density | 2.8629 | Kg/m3
Total heat @Required Pre. & Temp. at Outlet of De-Superheater | 666.8411 | Kcal/kg | Operating Pressure | 8 | Bar (g) |  |  |  | Enthalpy | 3448.9133 | KJ/Kg |  | Enthalpy | 2790.0633 | KJ/Kg |  | Specific volume | 0.3493 | m3/kg
Sp. Volume @Inlet Superheated Pre. & Temp. | 0.07488 | m3/kg | Operating Temperature | 415 | Deg C | OUTLET Desuperheater SIZE |  |  | Enthalpy | 824.3101 | Kcal/Kg |  | Enthalpy | 666.8411 | Kcal/Kg
Sp. Volume @Outlet Superheated Pre. & Temp. | 0.3493 | m3/kg | Line Size | 500 | NB | Flow | 4804.8246 | m³/hr | Density | 13.3546 | Kg/m3 |  | Density | 4.5297 | Kg/m3
Sp. Volume @Outlet of De-Superheater Pr. & Temp. | 0.22076 | m3/kg | MOC TABLE | MOC | CLASS |  | 1.3347 | m³/sec | Specific volume | 0.07488 | m3/kg |  | Specific volume | 0.22076 | m3/kg
|  |  | Flange/Forged Products | A182 Gr. F11 | FL 300 | Diameter of Pipe | 0.29914 | mtr | Diameter of pipe | 0.18038 | m |  | Diameter of pipe | 0.30972 | m
Available extra heat in per kg of Steam | 157.4689 | Kcal/kg | Valve/Srainer/Casted Product | ASTM A217 WC6 | FL 300 |  | 299.141 | mm | Diameter of Pipe | 180.3799 | mm |  | Diameter of Pipe | 309.7184 | mm
Available extra heat in total Steam | 2676971.992 | Kcal/hr | Pipe/Bend/Reducers | A335 Gr. P11 | SCHEDULE 20
Heat Gain by Water | 561.8411 | Kcal/kg |  |  |  | WATER INLET TO Desuperheater SIZE
|  |  | DE-SUPERHEATER ASSEMBLY |  | UNIT | Flow | 4.7646 | m³/hr
Required Water Quantity for Desuperheating the Steam | 4764.6422 | Kg/hr | Operating Pressure | 10 | Bar (g) |  | 0.0013235 | m³/sec
STEAM VELOCITY AT INLET | 28 | m/s | Operating Temperature | 105 | Deg C | Diameter of Pipe | 0.029034 | mtr
PRDS INLET CALCULATED LINE SIZE | 126.8363 | mm | Line Size | 40 | NB |  | 29.0345 | mm
STEAM VELOCITY AT PRS OUTLET | 23.5 | m/s | MOC TABLE | MOC | CLASS
CALCULATED LINE SIZE AT THE OUTLET OF PRS | 299.023 | mm | Flange/Forged Products | A105 | FL 150
STEAM VELOCITY AT DESUPERHEATER OUTLET | 19 | m/s | Valve/Srainer/Casted Product | ASTM A216 WCB | FL 150
CALCULATED LINE SIZE AT THE OUTLET OF DESUPERHEATER | 299.141 | mm | Pipe/Bend/Reducers | A106 Grade B | SCHEDULE 80
WATER INJECTION VELOCITY AT DESUPERHEATER | 2 | m/s
CALCULATED LINE SIZE FOR WATER | 29.0345 | mm
Input Fields
Result
Please refer the below link for Superheated Steam Table
https://www.tlv.com/global/TI/calculator/superheated-steam-table.html

## AIR PIPE (hidden)
https://toolbox.tlv.com/global/TI/calculator/air-pipe-sizing-velocity.html#
| Parameters | Details | Unit
| Air Flow | 167 | Nm3/min | A
| Air Density | 1.22 | kg/m3 | B
| Sp Heat | 0.2402 | kcal/kg⋅°C | C
| Inlet Temp | 40 | Deg C | D
| Outlet Temp | 20 | Deg C | E
| Cooling Load | 58726.0176 | kCal/hr | F = AX60XBXCX(D-E)
| Chilled Water In Temp | 7 | Deg C | G
| Chilled Water out Temp | 12 | Deg C | H
| Chilled Water Flow Rate | 11745.2035 | kg/hr | P = F/(H-G)

## Sheet46 (hidden)
Hot Water Flow Rate | 35000 | kg/hr
Return Temp from Process | 95 | Deg C
Supply Temp to Process | 100 | Deg C
Diff. Temp | 5 | Deg C
Total Heat Load | 175000 | kCal/hr
Steam PRessure | 3.5 | bar (g)
Steam Latent Heat | 510 | kCal/kg
Steam Consumption | 343.1373 | kg/hr
Equivalent Electrical Load | 254.1875 | kW

## Sheet30 (hidden)
| FL 150 | FL 150 | FL 150 | FL 300 | FL 300 | FL 300 | FL 600 | FL 600 | FL 600 | FL 900 | FL 900 | FL 900
Temp (°F) | ASTM A216 WCB | ASTM A217 WC6 | ASTM A217 WC9 | ASTM A216 WCB | ASTM A217 WC6 | ASTM A217 WC9 | ASTM A216 WCB | ASTM A217 WC6 | ASTM A217 WC9 | ASTM A216 WCB | ASTM A217 WC6 | ASTM A217 WC9
| A105 | A182 Gr. F11 | A182 Gr. F22 | A105 | A182 Gr. F11 | A182 Gr. F22 | A105 | A182 Gr. F11 | A182 Gr. F22 | A105 | A182 Gr. F11 | A182 Gr. F22
| A106 Grade B | A335 Gr. P11 | A182 Gr. P22 | A106 Grade B | A335 Gr. P11 | A182 Gr. P22 | A106 Grade B | A335 Gr. P11 | A182 Gr. P22 | A106 Grade B | A335 Gr. P11 | A182 Gr. P22
-29 to 38 | 19.6 |  |  | 51.1 |  |  | 102.1 |  |  | 153.2
50 | 19.2 |  |  | 50.1 |  |  | 100.2 |  |  | 150.4
100 | 17.7 |  |  | 46.6 |  |  | 93.2 |  |  | 139.8
150 | 15.8 |  |  | 45.1 |  |  | 90.2 |  |  | 135.2
200 | 13.8 |  |  | 43.8 |  |  | 87.6 |  |  | 131.4
250 | 12.1 |  |  | 41.9 |  |  | 83.9 |  |  | 125.8
300 | 10.2 |  |  | 39.8 |  |  | 79.6 |  |  | 119.5
325 | 9.3 |  |  | 38.7 |  |  | 77.4 |  |  | 116.1
350 | 8.4 |  |  | 37.6 |  |  | 75.1 |  |  | 112.7
375 | 7.4 |  |  | 36.4 |  |  | 72.7 |  |  | 109.1
400 | 6.5 | 6.5 | 6.5 | 34.7 | 36.5 | 36.5 | 69.4 | 73.3 | 73.3 | 104.2 | 109.8 | 109.8
425 | 5.5 | 5.5 | 5.5 | 28.8 | 35.2 | 35.2 | 57.5 | 70 | 70 | 86.3 | 105.1 | 105.1
450 | 4.6 | 4.6 | 4.6 | 23 | 33.7 | 33.7 | 46 | 67.7 | 67.7 | 69 | 101.4 | 101.4
475 | 3.7 | 3.7 | 3.7 | 17.4 | 31.7 | 31.7 | 34.9 | 63.4 | 63.4 | 52.3 | 95.1 | 95.1
500 | 2.8 | 2.8 | 2.8 | 11.8 | 25.7 | 28.2 | 23.5 | 51.5 | 56.5 | 35.3 | 77.2 | 84.7
538 | 1.4 | 1.4 | 1.4 | 5.9 | 14.9 | 18.4 | 11.8 | 29.8 | 36.9 | 17.7 | 44.7 | 55.3
550 | - | 1.4 | 1.4 | - | 12.7 | 15.6 | - | 25.4 | 31.3 | - | 38.1 | 46.9
575 | - | 1.4 | 1.4 | - | 8.8 | 10.5 | - | 17.6 | 21.1 | - | 26.4 | 31.6
600 | - | 1.4 | 1.4 | - | 6.1 | 6.9 | - | 12.2 | 13.8 | - | 18.3 | 20.7
625 | - | 1.4 | 1.4 | - | 4.3 | 4.5 | - | 8.5 | 8.9 | - | 12.8 | 13.4
650 | - | 1.1 | 1.1 | - | 2.8 | 2.8 | - | 5.7 | 5.7 | - | 8.5 | 8.5
675 | - | - | - | - | - | - | - | - | - | - | - | -

## Sheet4
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
SATURATED STEAM TABLE in S.I. Units
Gauge Pressure | Boiling Point | Specific Volume | Density | Sensible Heat | Latent Heat | Total Heat | INDEX
( bar (g) ) | (Deg C) | (m3/kg) | (kg/m3) | (kcal/kg) | (kcal/kg) | (kcal/kg)
0 | 99.63 | 1.694 | 0.59 | 99.72 | 539.3 | 639.02
0.1 | 102.32 | 1.549 | 0.645 | 102.43 | 537.59 | 640.01
0.2 | 104.81 | 1.428 | 0.7 | 104.94 | 535.99 | 640.93
0.3 | 107.13 | 1.325 | 0.755 | 107.29 | 534.49 | 641.77
0.4 | 109.32 | 1.236 | 0.809 | 109.49 | 533.07 | 642.56
0.5 | 111.37 | 1.159 | 0.863 | 111.57 | 531.73 | 643.3
0.6 | 113.32 | 1.091 | 0.916 | 113.54 | 530.45 | 643.99
0.7 | 115.17 | 1.031 | 0.97 | 115.42 | 529.22 | 644.64
0.8 | 116.93 | 0.977 | 1.023 | 117.2 | 528.05 | 645.25
0.9 | 118.62 | 0.929 | 1.076 | 118.91 | 526.92 | 645.83
1 | 120.2 | 0.885 | 1.13 | 120.77 | 525.79 | 646.57
1.1 | 121.8 | 0.846 | 1.182 | 122.34 | 524.75 | 647.1
1.2 | 123.3 | 0.81 | 1.235 | 123.85 | 523.75 | 647.6
1.3 | 124.7 | 0.777 | 1.287 | 125.3 | 522.79 | 648.09
1.4 | 126.1 | 0.746 | 1.34 | 126.7 | 521.85 | 648.56
1.5 | 127.4 | 0.718 | 1.393 | 128.08 | 520.93 | 649
1.6 | 128.7 | 0.693 | 1.443 | 129.3 | 520.05 | 649.43
1.7 | 129.9 | 0.668 | 1.497 | 130.6 | 519.18 | 649.84
1.8 | 131.2 | 0.646 | 1.548 | 131.9 | 518.34 | 650.24
1.9 | 132.4 | 0.625 | 1.6 | 133.1 | 517.52 | 650.63
2 | 133.5 | 0.606 | 1.65 | 134.2 | 516.72 | 651
2.1 | 134.6 | 0.587 | 1.704 | 135.4 | 515.93 | 651.36
2.2 | 135.7 | 0.57 | 1.754 | 136.5 | 515.17 | 651.7
2.3 | 136.8 | 0.554 | 1.805 | 137.6 | 514.41 | 652.04
2.4 | 137.8 | 0.538 | 1.859 | 138.6 | 513.68 | 652.36
2.5 | 138.8 | 0.524 | 1.908 | 139.72 | 512.96 | 652.68
2.6 | 139.8 | 0.51 | 1.961 | 140.73 | 512.25 | 652.99
2.7 | 140.8 | 0.497 | 2.012 | 141.7 | 511.56 | 653.28
2.8 | 141.8 | 0.486 | 2.058 | 142.7 | 510.87 | 653.57
2.9 | 142.7 | 0.473 | 2.114 | 143.65 | 510.2 | 653.86
3 | 143.6 | 0.462 | 2.1645 | 144.58 | 509.54 | 654.13
3.1 | 144.6 | 0.45 | 2.2222 | 145.5 | 508.9 | 654.4
3.2 | 145.4 | 0.441 | 2.2676 | 146.39 | 508.26 | 654.66
3.3 | 146.3 | 0.43 | 2.3256 | 147.27 | 507.63 | 654.91
3.4 | 147.1 | 0.423 | 2.3641 | 148.14 | 507.01 | 655.16
3.5 | 148 | 0.412 | 2.4272 | 148.99 | 506.4 | 655.403
3.6 | 148.7 | 0.405 | 2.4691 | 149.83 | 505.8 | 655.63
3.7 | 149.6 | 0.396 | 2.5253 | 150.65 | 505.21 | 655.86
3.8 | 150.3 | 0.39 | 2.5641 | 151.46 | 507.63 | 656.09
3.9 | 151.17 | 0.381 | 2.6247 | 152.25 | 504.05 | 656.31
4 | 151.8 | 0.375 | 2.6667 | 153.03 | 503.43 | 656.52
4.1 | 152.6 | 0.366 | 2.7322 | 153.8 | 502.92 | 656.73
4.2 | 153.3 | 0.361 | 2.7701 | 154.56 | 502.37 | 656.94
4.3 | 154.14 | 0.353 | 2.8329 | 155.31 | 501.82 | 657.14
4.4 | 154.7 | 0.348 | 2.8736 | 156.05 | 501.28 | 657.34
4.5 | 155.55 | 0.341 | 2.9326 | 156.77 | 500.75 | 657.53
4.6 | 156.2 | 0.337 | 2.9674 | 157.49 | 500.22 | 657.73
4.7 | 156.92 | 0.33 | 3.0303 | 158.2 | 499.7 | 657.9
4.8 | 157.5 | 0.326 | 3.0675 | 158.89 | 499.19 | 658.08
4.9 | 158.2 | 0.319 | 3.1348 | 159.58 | 498.67 | 658.26
5 | 158.8 | 0.315 | 3.1746 | 160.26 | 498.17 | 658.44
5.1 | 159.56 | 0.31 | 3.2258 | 160.93 | 497.67 | 658.61
5.2 | 160.1 | 0.306 | 3.268 | 161.59 | 497.18 | 658.78
5.3 | 160.83 | 0.3 | 3.3333 | 162.25 | 496.69 | 658.94
5.4 | 161.4 | 0.297 | 3.367 | 162.89 | 496.2 | 659.1
5.5 | 162.06 | 0.292 | 3.4247 | 163.53 | 495.72 | 659.26
5.6 | 162.6 | 0.288 | 3.4722 | 164.016 | 495.25 | 659.42
5.7 | 163.27 | 0.283 | 3.5336 | 164.79 | 494.78 | 659.57
5.8 | 163.8 | 0.28 | 3.5714 | 165.4 | 494.31 | 659.72
5.9 | 164.45 | 0.276 | 3.6232 | 166.01 | 493.85 | 659.87
6 | 165 | 0.273 | 3.663 | 166.6 | 493.39 | 660.01
6.1 | 165.6 | 0.268 | 3.7313 | 167.21 | 492.94 | 660.15
6.2 | 166.1 | 0.265 | 3.7736 | 167.8 | 492.49 | 660.29
6.3 | 166.7 | 0.261 | 3.8314 | 168.39 | 492.04 | 660.43
6.4 | 167.2 | 0.258 | 3.876 | 168.9 | 491.6 | 660.57
6.5 | 167.82 | 0.255 | 3.9216 | 169.54 | 491.16 | 660.7
6.6 | 168.3 | 0.252 | 3.9683 | 170.1 | 490.72 | 660.83
6.7 | 168.9 | 0.248 | 4.0323 | 170.66 | 490.29 | 660.96
6.8 | 169.4 | 0.246 | 4.065 | 171.22 | 489.87 | 661.09
6.9 | 169.9 | 0.242 | 4.1322 | 171.77 | 489.44 | 661.21
7 | 170.4 | 0.24 | 4.1667 | 172.31 | 489.02 | 661.34
7.1 | 170.99 | 0.237 | 4.2194 | 172.85 | 488.65 | 661.46
7.2 | 171.4 | 0.235 | 4.2553 | 173.39 | 488.19 | 661.58
7.3 | 172.02 | 0.231 | 4.329 | 173.92 | 487.77 | 661.69
7.4 | 172.4 | 0.229 | 4.3668 | 174.44 | 487.36 | 661.81
7.5 | 173 | 0.226 | 4.4248 | 174.96 | 486.96 | 661.92
7.6 | 173.4 | 0.224 | 4.4643 | 175.47 | 486.55 | 662.03
7.7 | 173.98 | 0.221 | 4.5249 | 175.99 | 486.15 | 662.14
7.8 | 174.4 | 0.219 | 4.5662 | 176.49 | 485.76 | 662.25
7.9 | 174.94 | 0.216 | 4.6296 | 176.99 | 485.36 | 662.36
8 | 175.4 | 0.215 | 4.6512 | 177.49 | 484.97 | 662.46
8.1 | 175.89 | 0.212 | 4.717 | 177.99 | 484.58 | 662.57
8.2 | 176.3 | 0.21 | 4.7619 | 178.48 | 484.19 | 662.67
8.3 | 176.81 | 0.207 | 4.8309 | 178.96 | 483.81 | 662.77
8.4 | 177.2 | 0.206 | 4.8544 | 179.44 | 483.42 | 662.87
8.5 | 177.7 | 0.203 | 4.9261 | 179.92 | 482.04 | 662.97
8.6 | 178.1 | 0.202 | 4.9505 | 180.39 | 482.67 | 663.07
8.7 | 178.62 | 0.199 | 5.0251 | 180.86 | 482.29 | 663.16
8.8 | 179 | 0.198 | 5.0505 | 181.33 | 481.92 | 663.25
8.9 | 179.5 | 0.195 | 5.1282 | 181.79 | 481.55 | 663.35
9 | 179.88 | 0.194 | 5.1546 | 182.14 | 481.18 | 663.44
9.1 | 180.3 | 0.192 | 5.2083 | 182.76 | 482.81 | 663.53
9.2 | 180.8 | 0.1904 | 5.2521 | 183.16 | 480.452 | 663.62
9.3 | 181.23 | 0.188 | 5.3191 | 183.61 | 480.09 | 663.7
9.4 | 181.653 | 0.186 | 5.3763 | 184.06 | 479.73 | 663.79
9.5 | 182.01 | 0.18 | 5.5556 | 184.5 | 479.4 | 663.869
9.6 | 182.48 | 0.183 | 5.4645 | 184 | 479.01 | 663.96
9.7 | 182.9 | 0.181 | 5.5249 | 185.38 | 478.662 | 664.04
9.8 | 183.31 | 0.18 | 5.5556 | 185.81 | 478.3 | 664.12
9.9 | 183.71 | 0.178 | 5.618 | 186.25 | 477.95 | 664.2
10 | 184.06 | 0.177 | 5.6497 | 186.57 | 477.35 | 663.91
10.5 | 186.1 | 0.169 | 5.91 | 188.77 | 475.89 | 664.661
11 | 187.96 | 0.163 | 6.127 | 190.7 | 473.94 | 664.64
11.5 | 189.86 | 0.156 | 6.41 | 192.77 | 472.58 | 665.355
12 | 191.6 | 0.151 | 6.617 | 194.58 | 470.7 | 665.29
12.5 | 193.4 | 0.145 | 6.896 | 196.55 | 469.42 | 665.965
13 | 195.04 | 0.141 | 7.106 | 198.26 | 467.6 | 665.85
13.5 | 196.73 | 0.136 | 7.35 | 200.12 | 466.39 | 666.504
14 | 198.28 | 0.132 | 7.596 | 201.74 | 464.61 | 666.35
14.5 | 199.89 | 0.127 | 7.87 | 203.519 | 463.466 | 666.97
15 | 201.37 | 0.124 | 8.085 | 205.06 | 461.74 | 666.79
15.5 | 202.9 | 0.12 | 8.33 | 206.76 | 460.644 | 667.399
16 | 204.3 | 0.117 | 8.575 | 208.23 | 458.95 | 667.18
16.5 | 205.77 | 0.11 | 9.09 | 209.863 | 457.911 | 667.76
17 | 207.11 | 0.11 | 9.065 | 211.27 | 456.26 | 667.53
17.5 | 208.51 | 0.107 | 9.345 | 212.84 | 455.26 | 668.09
18 | 209.79 | 0.105 | 9.556 | 214.19 | 453.64 | 668.24
18.5 | 211.14 | 0.102 | 9.8 | 215.705 | 452.679 | 668.38
19 | 212.37 | 0.1 | 10.047 | 217.01 | 451.1 | 668.51
19.5 | 213.67 | 0.097 | 10.309 | 218.468 | 450.166 | 668.63
20 | 214.85 | 0.095 | 10.539 | 219.72 | 448.61 | 668.74
20.5 | 216.1 | 0.092 | 10.86 | 221.136 | 447.714 | 668.84
21 | 217.24 | 0.091 | 11.032 | 222.35 | 446.19 | 668.94
21.5 | 218.85 | 0.088 | 11.36 | 223.719 | 445.318 | 669.03
22 | 219.55 | 0.087 | 11.525 | 224.89 | 443.82 | 669.117
22.5 | 220.72 | 0.084 | 11.9 | 226.22 | 442.97 | 669.19
23 | 221.78 | 0.083 | 12.02 | 227.36 | 441.5 | 669.26
23.5 | 222.91 | 0.081 | 12.34 | 228.652 | 440.67 | 669.32
24 | 223.94 | 0.08 | 12.515 | 229.75 | 439.23 | 669.38
24.5 | 225.04 | 0.078 | 12.82 | 231.014 | 438.424 | 669.43
25 | 226.03 | 0.077 | 13.012 | 232.08 | 437.01 | 669.48
25.5 | 227.03 | 0.075 | 13.33 | 233.313 | 436.212 | 669.52
26 | 228.06 | 0.074 | 13.509 | 234.35 | 434.82 | 669.56
26.5 | 229.11 | 0.072 | 13.88 | 235.553 | 434.04 | 669.51
27 | 230.04 | 0.071 | 14.008 | 236.57 | 432.67 | 669.617
27.5 | 231.06 | 0.07 | 14.28 | 237.74 | 431.901 | 669.63
28 | 231.96 | 0.069 | 14.508 | 238.73 | 430.56 | 669.65
28.5 | 232.95 | 0.067 | 14.92 | 239.87 | 429.79 | 669.668
29 | 233.88 | 0.0666 | 15.015 | 240.91 | 428.75 | 669.67
29.5 | 234.8 | 0.0655 | 15.267 | 241.95 | 427.72 | 669.68
30 | 235.7 | 0.0644 | 15.528 | 242.98 | 426.7 | 669.68
30.5 | 236.6 | 0.0634 | 15.773 | 243.99 | 425.68 | 669.67
31 | 237.48 | 0.0624 | 16.026 | 245 | 424.67 | 669.67
31.5 | 238.36 | 0.0614 | 16.287 | 245.99 | 423.66 | 669.65
32 | 239.22 | 0.0605 | 16.529 | 246.97 | 422.67 | 669.64
32.5 | 240.07 | 0.0596 | 16.779 | 247.94 | 421.68 | 669.62
33 | 240.92 | 0.0587 | 17.036 | 248.91 | 420.69 | 669.6
33.5 | 241.75 | 0.0578 | 17.301 | 249.86 | 419.71 | 669.57
34 | 242.58 | 0.057 | 17.544 | 250.81 | 418.74 | 669.55
34.5 | 243.4 | 0.0562 | 17.794 | 251.74 | 417.77 | 669.52
35 | 244.2 | 0.0554 | 18.051 | 252.67 | 416.81 | 669.48
35.5 | 245.01 | 0.0546 | 18.315 | 253.58 | 415.85 | 669.44
36 | 245.79 | 0.0538 | 18.587 | 254.49 | 414.91 | 669.41
36.5 | 246.58 | 0.0531 | 18.832 | 255.4 | 413.96 | 669.36
37 | 247.35 | 0.0524 | 19.084 | 256.29 | 413.02 | 669.31
37.5 | 248.12 | 0.0517 | 19.342 | 257.18 | 412.08 | 669.27
38 | 248.88 | 0.0511 | 19.581 | 258.06 | 411.15 | 669.21
38.5 | 249.66 | 0.0504 | 19.841 | 258.93 | 410.23 | 669.16
39 | 250.3 | 0.0497 | 20.121 | 259.8 | 409.3 | 669.11
39.5 | 251.11 | 0.0491 | 20.367 | 260.65 | 408.39 | 669.05
40 | 251.84 | 0.0485 | 20.619 | 261.51 | 407.48 | 668.98
40.5 | 252.56 | 0.0479 | 20.877 | 262.35 | 406.57 | 668.92
41 | 253.28 | 0.0473 | 21.142 | 263.19 | 405.66 | 668.85
41.5 | 253.99 | 0.0467 | 21.413 | 264.02 | 404.76 | 668.79
42 | 254.7 | 0.0461 | 21.692 | 264.84 | 403.87 | 668.72
42.5 | 255.4 | 0.0456 | 21.93 | 265.66 | 402.97 | 668.64
43 | 256.09 | 0.0451 | 22.183 | 266.48 | 402.09 | 668.57
43.5 | 256.77 | 0.0446 | 22.442 | 267.29 | 401.21 | 668.49
44 | 257.45 | 0.044 | 22.707 | 268.09 | 400.32 | 668.41
44.5 | 258.13 | 0.0435 | 22.989 | 268.88 | 399.45 | 668.33
45 | 258.8 | 0.043 | 23.234 | 269.68 | 398.57 | 668.25
45.5 | 259.46 | 0.0426 | 23.496 | 270.46 | 397.7 | 668.17
46 | 260.12 | 0.0421 | 23.764 | 271.24 | 396.83 | 668.08
46.5 | 260.77 | 0.0416 | 24.038 | 272.02 | 395.97 | 667.99
47 | 261.42 | 0.0412 | 24.295 | 272.79 | 395.11 | 667.9
47.5 | 262.06 | 0.0407 | 24.558 | 273.55 | 394.25 | 667.81
48 | 262.7 | 0.0403 | 24.826 | 274.32 | 393.4 | 667.71
48.5 | 263.33 | 0.0398 | 25.126 | 275.07 | 392.54 | 667.61
49 | 263.96 | 0.0394 | 25.361 | 275.82 | 391.69 | 667.52
49.5 | 264.58 | 0.039 | 25.628 | 276.57 | 390.85 | 667.41
50 | 265.2 | 0.0386 | 25.9 | 277.31 | 390 | 667.31
67 | 283.88 | 0.0282 | 16 | 300.317 | 362.63 | 662.95

## Sheet5
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
BOILER DIRECT EFFICIENCY CALCULATOR
Steam Generation | 1600 | kg/hr |  | INDEX
Boiler Pressure | 7 | bar (g)
Boiler Fuel Used | Coal
GCV of Fuel | 4500 | Kcal/kg
Price of Fuel | 9.5 | Rs./kg
Fuel Consumption | 112 | kg/hr
Boiler Feed Water Temperature | 65 | Deg C
Total Heat of Steam @ Boiler Pressure | 661.34 | Kcal/kg | 596.34
954144
Direct Efficinency of Boiler | 78 | %
Steam Cost | 0.665 | Rs./kg
Input Fields
Result

## Sheet6
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
Blow Down Saving Calculator
Type of Boiler | PACKAGED SMOKE TUBE BOILER |  | INDEX
Boiler Capacity | 2000 | kg/hr
Average Steam Generation | 2000 | kg/hr
Fuel | COAL
Price of Fuel | 8 | Rs./kg
GCV of Fuel | 5000 | Kcal/kg
Boiler Working Pressure | 12 | bar (g)
Boiler Efficiency | 70 | %
Feed Water TDS | 500 | ppm
Boiler Allowable TDS | 1000 | ppm
Duration of manual Blow Down | 10 | sec.
No. of Manual Blow down per day | 3 | no./day
Water flow through B/D Valve @ boiler Pressure | 6 | kg/s
Heat content in Blow Down @ Boiler Pressure (i.e. temp @ boiler pressure) | 198.28 | Kcal/kg
Operational days per month | 30 | days/month
Operational months per year | 12 | months/year
Required Blow Down for Boiler | 48000 | kg/day
Present Manual Blow Down | 180 | kg/day
Excess Blow Down per day | -47820 | kg/day
Equivalnt Saving from reduction in Blow down in Rs. | -21672.5705 | Rs./day
| -650177.1154 | Rs./month
| -7802125.385 | Rs./year
Input Fields
Result

## Sheet7
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
Steam Required for Process Heating
Process Media | water |  | INDEX
Process Media Flowrate | 2000 | kg/hr
Process Media Initial Temp. | 30 | Deg C
Process Media Final Tepmp. | 80 | Deg C
Specific Heat of Process Media | 1 | Kcal/kg. Deg C
Steam Pressure | 3 | bar (g)
Latent Heat of Steam @ given pressure | 509.54 | Kcal/kg
Steam Required for Heating process media | 196.2554 | kg/hr
Input Fields
Result

## Copy of Sheet6 (hidden)
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
Blow Down Saving Calculator
Type of Boiler | SOLID FUEL |  | INDEX
Boiler Capacity | 10000 | kg/hr
Average Steam Generation | 6000 | kg/hr
Fuel | CHILLI RESIDUE
Price of Fuel | 3 | Rs./kg
GCV of Fuel | 3200 | Kcal/kg
Boiler Working Pressure | 15 | bar (g)
Boiler Efficiency | 70 | %
Feed Water TDS | 100 | ppm
Boiler Allowable TDS | 3500 | ppm
Duration of manual Blow Down | 60 | sec.
No. of Manual Blow down per day STEAM DRUM | 3 | no./day
Water flow through B/D Valve @ boiler Pressure | 15 | kg/s
No. of Manual Blow down per day PIPE | 6 | no./day
Water flow through B/D Valve @ boiler Pressure | 8 | kg/s
No. of Manual Blow down per day BOTTOM HEADER | 9 | no./day
Water flow through B/D Valve @ boiler Pressure | 3 | kg/s
Heat content in Blow Down @ Boiler Pressure (i.e. temp @ boiler pressure) | 201 | Kcal/kg
Operational days per month | 30 | days/month
Operational months per year | 12 | months/year
Required Blow Down for Boiler | 4235.2941 | kg/day
Present Manual Blow Down | 7200 | kg/day
Excess Blow Down per day | 2964.7059 | kg/day
Equivalnt Saving from reduction in Blow down in Rs. | 798.0882 | Rs./day
| 23942.6471 | Rs./month
| 287311.7647 | Rs./year
Input Fields
Result

## Sheet8
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
Steam required for Evaporation
Process Media | Water |  |  | INDEX
Process Media total Quantity | 2722 | kg
Process Media Qty for evaporation | 222 | kg
Evaporation Pressure | 0.5 | bar (g)
Temp.@ evaporation pressure | 111.37 | Deg C
Latent Heat @ evaporation pressure | 531.73 | Kcal/kg
Initial Temp. of process media | 50 | Deg C
Specific Heat of Process Media | 1 | Kcal/kg.Deg C
Steam Pressure | 3 | bar (g)
Latent Heat of Steam @ given pressure | 509.54 | Kcal/kg
Energy req.for Process media to reach upto boiling point (Q1) | 167049.14 | Kcal (A) | TOTAL INPUT X SP. HEAT X (BOILING TEMP - INITIAL TEMP)
Energy req.to evaporate given qty of process media (Q2) | 118044.06 | Kcal (B) | TOTAL EVAP QTY X LATENT HEAT OF EVAPORISATION
Total Energy required (Q) for evaporation | 285093.2 | Kcal (A+B)
Steam Qty req. to evaporate given qty of process media | 559.5109 | kg/hr
EQUIVALENT ELECTRICAL LOAD | 331.2783 | kW

## Sheet9
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
Final Temp. of Feed Water Tank
Condensate Quantity | 6000 | Kg | INDEX
Condensate Temp. | 90 | Deg C
Fresh Water Quantity | 6000 | Kg
Fresh Water Temp. | 25 | Deg C
Flash Steam Quantity | 300 | Kg
Flash Steam Pressure | 0.5 | bar (g)
Total Heat of Flash Steam @given pressure | 643.3 | Kcal/kg
Total Quantity of mixed Fluids | 12300 | Kg
Total Heat in mixed Fluids | 882990 | Kcal
Final Temp. of Mixed Fluids | 71.7878 | Deg C
Input Fields
Result

## Sheet10
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
Rectangular Tank |  |  | Circular Tank |  |  |  | INDEX
Capacity |  | m3 | Capacity | 2 | m3
Length |  | m | Diameter | 1 | m | 2.5478
Width |  | m
|  |  | Length / Height | 2.5478 | m
Height | #DIV/0! | m
Rectangular Tank |  |  | Circular Tank |  |  |  | INDEX | Input Fields
Length |  | m | Length / Height | 2.6 | m |  |  | Result
Width |  | m | Diameter | 1.5 | m
Height |  | m
|  |  | Volume | 4.5922 | m3
Volume | 0 | m3
Weight Calculator (Rectangular Tank) |  |  | Weight Calculator (Cicular Tank)
Capacity |  | m3 | Capacity of Tank | 4.59 | m3
Length |  | m | Dia of tank | 1.5 | m
Width |  | m | Thickness of tank | 0.006 | m
Density |  | kg/m3 | Density | 7850 | kg/m3
Thickness |  | m | Length / Height of tank | 2.6 | m
Height |  | m
|  |  | Circumference of tank | 4.71 | m
Total sides of tank | 6 | nos | Volume of tank sheet Req | 0.073476 | m3
Weight of 2 sides | 0 | kg | Weight of tank | 576.7866 | kg
Weight of 2 sides | 0 | kg
Weight of 2 sides | 0 | kg | No of Side plates | 2 | nos
|  |  | Side Plate Volume | 0.006 | m3
Total weight of tank | 0 | kg | Total Weight of side plates | 94.2 | kg
|  |  | Total Weight | 670.9866 | kg
TUBE / PIPE SURFACE AREA
|  |  | Length / Height | 1.6 | m
|  |  | Diameter | 0.019 | m
|  |  | SURFACE AREA | 0.095456 | M2

## Sheet11
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
HOT WATER GENERATION SYSTEM (Heating & Cooling)
Heating application |  |  | INDEX
Hot Water Flow rate | 25 | m3/hr |  | Input Fields
Hot Water Inlet Temp. | 85 | Deg C |  | Result
Hot Water Outlet Temp. | 95 | Deg C
Specific Heat of Water | 1 | kcal/kg deg C
Steam Pressure | 3.5 | bar g
Latent Heat of Steam @ given pressure | 506.4 | Kcal/kg
Req. steam qty for Heating | 493.6809 | Kg/hr
Steam Flow Rate | 493.6809 | kg/hr
Steam Pressure | 3.5 | bar (g)
Steam Specific Volume | 0.412 | m3/kg
Steam Flow Rate | 203.3965 | m3/hr
| 0.056499 | m³/sec
Steam Velocity | 25 | m/s
Diameter of Pipe | 0.053656 | mtr
Steam Line Size | 53.6557 | mm
Hot Water Flow rate | 25 | m³/hr
| 0.0069444 | m³/sec
Water Velocity | 1.5 | m/s
Hot Water Line Size | 0.076796 | mtr
| 76.7959 | mm
Cooling application
Cooling Water Flow rate |  | m3/hr
Cooling Water Inlet Temp. |  | Deg C
Cooling Water Outlet Temp. |  | Deg C
Specific Heat of Water | 1 | kcal/kg deg C
Chilled Water Inlet Temp. |  | Deg C
Chilled Water Outlet Temp. |  | Deg C
Chilled Water Flow rate | #DIV/0! | m3/hr
Cooling Water Flow rate |  | m³/hr
| 0 | m³/sec
Velocity |  | m/s
Cooling Water Line Size | #DIV/0! | mtr
| #DIV/0! | mm
Chilled Water Flow rate | #DIV/0! | m³/hr
| #DIV/0! | m³/sec
Velocity | 1.5 | m/s
Chilled Water Line Size | #DIV/0! | mtr
| #DIV/0! | mm

## 12 Safety Valve
SAFETY VALVE ORIFICE CALCULATION
C | Consatnt | 0.38
P | Set Pressure | 4.1 | Bar(G)
E | Required Relief Capacity | 2600 | Kg/Hr |  | INDEX
F | Super Heat Correction Factor. 1 is for saturated steam | 1
| Area Calculation | 1338.1782
A | Calculated Throat/ Flow Area | 1338.1782 | mm2 | A =(E / (C X (P+1.013)) X F
220
D | Calculated Throat/ Flow Diameter | 41.2878 | mm | D = √'(A X4 /3.14)

## 13 Weight Calculator
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
Weight Calculator for Pipe, Plate, Tube, C & I section and Angle
Weight Calculation For Pipe | [5 empty] | INDEX | Input Fields
Input | Value | Unit |  |  |  |  | Result
Density | 7850 | kg/m3
Outer Diameter | 2400 | mm
Thickness | 14 | mm
length | 3.4 | m
Values in meter
Inner Diameter | 2.372 | m
Outer Diameter | 2.4 | m
Thickness | 0.014 | m
Intermediate Calculations
Cross sectional Area | 0.10489 | m2
Volume | 0.35662 | m3
Result
Weight | 2799.4757 | kg
Weight Calculation For Bar Rod
Input | Value | Unit
Density | 7850 | kg/m3
length | 0.008 | m
Diameter OD | 340 | mm
Diameter OD | 0.34 | 3
0.785
Result
Weight | 5.6988 | kg
Weight Calculation For Plate
Input | Value | Unit
Density | 7850 | kg/m3
length | 2500 | mm
Thickness | 30 | mm
width | 1250 | mm
length | 2.5 | m
Thickness | 0.03 | m
width | 1.25 | m
Result
Weight | 735.9375 | kg
Weight Calculation For Square Tube |  |  | Weight Calculation For Rectangular Tube
Input | Value | Unit | Input | Value | Unit
Density | 7850 | kg/m3 | Density | 7850 | kg/m3
length | 1 | m | length | 1 | m
Thickness | 2 | mm | Thickness | 3 | mm
width | 50 | mm | width | 30 | mm
|  |  | Height | 50 | mm
Thickness | 0.002 | m | Thickness | 0.003 | m
width | 0.05 | m | width | 0.03 | m
|  |  | Height | 0.05 | m
Intermediate Calculations |  |  | Intermediate Calculations
Volume 1 | 0.0002 | m3 | Volume 1 | 0.00018 | m3
Volume 2 | 0.000184 | m3 | Volume 2 | 0.000264 | m3
Total Volume | 0.000384 | m3 | Total Volume | 0.000444 | m3
Result |  |  | Result
Weight | 3.0144 | kg | Weight | 3.4854 | kg
Weight Calculation For Channel Section
Input | Value | Unit
Density | 7850 | kg/m3
Length | 1 | m
Thickness | 5 | mm
Web Height | 75 | mm
Flange Length | 40 | mm
Values in Meter
Thickness | 0.005 | m
Web Height | 0.075 | m
Flange Length | 0.04 | m
Intermediate Calculations
Volume of Web | 0.000375 | m3
Volume of Flanges | 0.00035 | m3
Total Volume | 0.000725 | m3
Result
Weight | 5.6913 | kg
Weight Calculation For I Section
Input | Value | Unit
Density | 7850 | kg/m3
Length | 1 | m
Height | 100 | mm
Width | 50 | mm
Web Thickness (t) | 4.5 | mm
Flange Thickness (T) | 6.8 | mm
Values in Meter
Height | 0.1 | m
Width | 0.05 | m
Web Thickness (t) | 0.0045 | m
Flange Thickness (T) | 0.0068 | m
Intermediate Calculations
Volume of Web | 0.0003888 | m3
Volume of Flanges | 0.00068 | m3
Total Volume | 0.0010688 | m3
Result
Weight | 8.3901 | kg
Weight Calculation For Equal Angles
Input | Value | Unit
Density | 7850 | kg/m3
length | 18.6 | m
Thickness | 5 | mm
Sides | 50 | mm
Thickness | 0.005 | m
Sides | 0.05 | m
Volume 1 | 0.00465 | m3
Volume 2 | 0.004185 | m3
volume | 0.008835 | m3
Result
Weight | 69.3547 | kg

## 14 Pipe Thk. Calculator
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
PIPE WALL THICKNESS CALCULATOR ASME B31.3 |  |  |  | CALCULATIONS
Pipe Type | Seamless |  | INDEX | Symbol | Description | Value | Unit | Remark
Material of Construction | Carbon Steel |  |  | P | Operating Pressure | 1 | Mpa | Internal Design Pressure
Grade of Material | A106 Gr. B |  |  | D | Outside Diameter of Pipe | 168.3 | mm | From ASME B36.10
Internal design Pressure(g) | 10 | bar |  | S | Allowable Stress | 118 | Mpa | Stress Value of Material From ASME SEC II D (2010) Page no: 10(CS WCB), 86(SS CF8) We Take 80% of Maximum Allowabel Stress In Calculation
Operating Temperature | 200 | °C |  | E | Quality Factor | 1 |  | Quality Factor From Tabel A-1A or Tabel A-1B of ASME B31.3
Size of Pipe | 150 | NB |  | W | Strength Reduction Factor | 1 |  | Weid Joint Strength Reducing Factor in accordance with Para 3.2.2.5(e)
Schedule of Pipe / Class / Wall Thicknesses | 40 | In Case of IS3589 and A516 Gr. 70 Select the required thickness from Drop-down |  | Y | Coefficient Y | 0.4 |  | Coefficient From Tabel 304.1.1
RESULTS |  |  |  | t | Calculated Wall Thickness | 0.88766 | mm | Pressure designed Thickness in Accordance with ASME B31.3(304.1.2)
Minimum Required Thickness (tm) | 2.3877 | mm |  | d1 | Major Diameter of Threading | Value Not Available | mm | In Accordance with BS21:1973
Actual Pipe Wall Thickness | 7.11 | mm |  | d2 | Minor Diameter of Threading | Value Not Available | mm | In Accordance with BS21:1973
HENCE REQUIRED WALL THICKNESS(tm) FOR THE SPECIFIDE OPERATING PARAMETER IS LESS THAN ACTUAL WALL THICKNESS(T) SO DESIGN IS SAFE |  |  |  | C | Sum of Mechanical Allowance | 1.5 | mm
|  |  |  | tm | Minimum Required Thickness (t+c) | 2.3877 | mm
|  |  |  | T | Actual Pipe Wall Thickness | 7.11 | mm
SAFE
NOT SAFE
SCHEDULE NOT AVAILABLE
NOT PERMISSIBLE

## 15 F&A Calculator
Details | Values | Unit | INDEX
Boiler Operating Pressure | 17 | Kg/cm2
Total Heat in Steam | 667.53 | kCal/kg
Boiler Capacity | 12000 | kg/hr
Feed Water Temp | 60 | °C
Latent heat (Atmoshperic pressure) | 540 | kCal/kg
Diffrence in F&A and Actual Latent heat | 0.12506
Diffrence * Boiler Capacity | 1500.6667
Boiler Delivery of Net Steam as per F&A 100 | 10499.3333 | kg/hr

## Material_Stress (hidden)
MAXIMUM ALLOWABLE STRESS VALUES | [6 empty] | COEFFICIENT FROM TABLE 304.1.1
Material Grade | Carbon Steel |  |  |  | Stainless Steel |  | Material Grade | Carbon Steel |  |  |  | Stainless Steel
Temperature | A106 Gr. B | A516 Gr. 70 | IS1239 | IS3589 | SS304 | SS316 | Temperature | A106 Gr. B | A516 Gr. 70 | IS1239 | IS3589 | SS304 | SS316 | Carbon SteelSeamless | Carbon SteelSeamless | Carbon SteelERW | Stainless SteelSeamless | Stainless SteelERW
65 | 118 | 138 | 118 | 118 | 138 | 138 | 65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | A106 Gr. B | A106 Gr. B | A516 Gr. 70 | SS304 | SS304
100 | 118 | 138 | 118 | 118 | 137 | 138 | 100 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  | IS1239 | SS316 | SS316
125 | 118 | 138 | 118 | 118 | 134 | 138 | 125 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  | IS3589
150 | 118 | 138 | 118 | 118 | 130 | 138 | 150 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
175 | 118 | 138 | 118 | 118 | 128 | 136 | 175 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
200 | 118 | 138 | 118 | 118 | 126 | 134 | 200 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
225 | 118 | 138 | 118 | 118 | 124 | 130 | 225 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
250 | 118 | 138 | 118 | 118 | 122 | 126 | 250 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
275 | 118 | 137 | 118 | 118 | 119 | 123 | 275 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
300 | 118 | 136 | 118 | 118 | 116 | 119 | 300 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
325 | 118 | 132 | 118 | 118 | 114 | 116 | 325 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
350 | 117 | 128 | 117 | 117 | 111 | 114 | 350 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
375 | 105 | 123 | 105 | 105 | 109 | 112 | 375 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
400 | 88.9 | 101 | 88.9 | 88.9 | 107 | 111 | 400 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
425 | 75.3 | 83.8 | 75.3 | 75.3 | 105 | 110 | 425 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
450 | 62.7 | 67.1 | 62.7 | 62.7 | 103 | 108 | 450 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
475 | 45.5 | 51 | 45.5 | 45.5 | 101 | 108 | 475 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
500 | 31.6 | 33.6 | 31.6 | 31.6 | 99.3 | 107 | 500 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4
525 | 21.9 | 21.3 | 21.9 | 21.9 | 98 | 106 | 525 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4
550 | 12.7 | 12.9 | 12.7 | 12.7 | 93.3 | 105 | 550 | 0.7 | 0.7 | 0.7 | 0.7 | 0.4 | 0.4
575 | DATA NOT AVAILABLE | DATA NOT AVAILABLE | DATA NOT AVAILABLE | DATA NOT AVAILABLE | 79.6 | 99.8 | 575 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5
593 | DATA NOT AVAILABLE | DATA NOT AVAILABLE | DATA NOT AVAILABLE | DATA NOT AVAILABLE | DATA NOT AVAILABLE | DATA NOT AVAILABLE | 593 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5
600 | DATA NOT AVAILABLE | DATA NOT AVAILABLE | DATA NOT AVAILABLE | DATA NOT AVAILABLE | DATA NOT AVAILABLE | 80.3 | 600 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6
625 | DATA NOT AVAILABLE | DATA NOT AVAILABLE | DATA NOT AVAILABLE | DATA NOT AVAILABLE | DATA NOT AVAILABLE | 65.5 | 625 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
650 and above | DATA NOT AVAILABLE | DATA NOT AVAILABLE | DATA NOT AVAILABLE | DATA NOT AVAILABLE | DATA NOT AVAILABLE | 50.4 | 650 and above | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7

## Pipe_Data
Carbon Steel (A-106 Gr. B) | [5 empty] | Stainless Steel (SS304/SS316) | [6 empty] | Carbon Steel IS1239 : LIGHT |  |  |  | Carbon Steel A516 Gr. 70 |  |  | Carbon Steel IS3589 |  | MAJOR AND MINOR DIA OF THREADING | [6 empty] | Pipe SIze
Concatenation | Pipe Size (NB) | Pipe Schedule | Outside Diameter(mm) | Wall Thickness(mm) |  |  | Pipe Size (NB) | Pipe Schedule | Outside Diameter(mm) | Wall Thickness(mm) |  | A | Pipe Size (NB) | Outside Diameter(mm) | Wall Thickness(mm) |  | Pipe Size (NB) | Outside Diameter(mm) |  | Pipe Size (NB) | Outside Diameter(mm) | SIZE (NB) | SIZE (Inches) | MAJOR (EXT) | MINOR (INT) | Mechanical Allowance | Round- up | A106 Gr. B | A106 Gr. B | A516 Gr. 70 | IS1239 | IS3589 | SS304 | SS316
610 | 6 | 10 | 10.3 | 1.24 |  | 65 | 6 | 5 | 10.3 | N/A |  | 6A | 6 | 10.3 | 1.8 |  | 250 | 273 |  | 150 | 168.3 | 6 | 1/8" | 9.728 | 8.566 | 0.581 | 0.6 | 6 | 6 | 250 | 6 | 150 | 6 | 6
630 | 6 | 30 | 10.3 | 1.45 |  | 610 | 6 | 10 | 10.3 | 1.73 |  | 8A | 8 | 13.7 | 1.8 |  | 300 | 232.9 |  | 200 | 219.1 | 8 | 1/4" | 13.157 | 11.445 | 0.856 | 0.9 | 8 | 8 | 300 | 8 | 200 | 8 | 8
640 | 6 | 40 | 10.3 | 1.73 |  | 640 | 6 | 40 | 10.3 | N/A |  | 10A | 10 | 17.1 | 1.8 |  | 350 | 355.6 |  | 250 | 273 | 10 | 3/8" | 16.662 | 14.95 | 0.856 | 0.9 | 10 | 10 | 350 | 10 | 250 | 10 | 10
680 | 6 | 80 | 10.3 | 2.41 |  | 680 | 6 | 80 | 10.3 | 2.41 | ` | 15A | 15 | 21.3 | 2 |  | 400 | 406.4 |  | 300 | 232.9 | 15 | 1/2" | 20.955 | 18.631 | 1.162 | 1.2 | 15 | 15 | 400 | 15 | 300 | 15 | 15
810 | 8 | 10 | 13.7 | 1.65 |  | 85 | 8 | 5 | 13.7 | N/A |  | 20A | 20 | 26.7 | 2.3 |  | 450 | 457 |  | 350 | 355.6 | 20 | 3/4" | 26.441 | 24.117 | 1.162 | 1.2 | 20 | 20 | 450 | 20 | 350 | 20 | 20
830 | 8 | 30 | 13.7 | 1.85 |  | 810 | 8 | 10 | 13.7 | 1.65 |  | 25A | 25 | 33.4 | 2.6 |  | 500 | 508 |  | 400 | 406.4 | 25 | 1" | 33.249 | 30.29 | 1.4795 | 1.5 | 25 | 25 | 500 | 25 | 400 | 25 | 25
840 | 8 | 40 | 13.7 | 2.24 |  | 840 | 8 | 40 | 13.7 | 2.24 |  | 32A | 32 | 42.16 | 2.6 |  | 600 | 610 |  | 450 | 457 | 32 | 11/4" | 41.91 | 38.952 | 1.479 | 1.5 | 32 | 32 | 600 | 32 | 450 | 32 | 32
880 | 8 | 80 | 13.7 | 3.02 |  | 880 | 8 | 80 | 13.7 | 3.02 |  | 40A | 40 | 48.26 | 2.9 |  | 700 | 711 |  | 500 | 508 | 40 | 11/2" | 47.803 | 44.845 | 1.479 | 1.5 | 40 | 40 | 700 | 40 | 500 | 40 | 40
1010 | 10 | 10 | 17.1 | 1.65 |  | 105 | 10 | 5 | 17.1 | N/A |  | 50A | 50 | 60.3 | 2.9 |  | 800 | 813 |  | 600 | 610 | 50 | 2" | 59.614 | 56.656 | 1.479 | 1.5 | 50 | 50 | 800 | 50 | 600 | 50 | 50
1030 | 10 | 30 | 17.1 | 1.85 |  | 1010 | 10 | 10 | 17.1 | 1.65 |  | 65A | 65 | 73.03 | 3.2 |  | 900 | 914 |  | 700 | 711 | 65 | 21/2" | 75.184 | 72.226 | 1.479 | 1.5 | 65 | 65 | 900 | 65 | 700 | 65 | 65
1040 | 10 | 40 | 17.1 | 2.31 |  | 1040 | 10 | 40 | 17.1 | 2.31 |  | 80A | 80 | 88.9 | 3.2 |  |  |  |  | 800 | 813 | 80 | 3" | 87.884 | 84.926 | 1.479 | 1.5 | 80 | 80 |  | 80 | 800 | 80 | 80
1080 | 10 | 80 | 17.1 | 3.2 |  | 1080 | 10 | 80 | 17.1 | 3.2 |  | 100A | 100 | 114.3 | 3.6 |  |  |  |  | 900 | 914 | 100 | 4" | 113.03 | 110.072 | 1.479 | 1.5 | 100 | 100 |  | 100 | 900 | 100 | 100
155 | 15 | 5 | 21.3 | 1.65 |  | 155 | 15 | 5 | 21.3 | 1.65 |  |  | Carbon Steel IS1239 : MEDIUM | [8 empty] | 125 | 5" | 138.43 | 135.472 | 1.479 | 1.5 | 125 | 125 |  | 125 |  | 125 | 125
1510 | 15 | 10 | 21.3 | 2.11 |  | 1510 | 15 | 10 | 21.3 | 2.11 |  | B | Pipe Size (NB) | Outside Diameter(mm) | Wall Thickness(mm) | [6 empty] | 150 | 6" | 163.83 | 160.872 | 1.479 | 1.5 | 150 | 150 |  | 150 |  | 150 | 150
1530 | 15 | 30 | 21.3 | 2.41 |  | 1540 | 15 | 40 | 21.3 | 2.77 |  | 6B | 6 | 10.3 | 2 | [6 empty] | 200 | WE HAVE ASSUME THE VALUE SINCE THREADING IS NOT RECOMMENDED ABOVE THE 6" PIPE |  |  |  | 1.5 | 200 | 200 |  |  |  | 200 | 200
1540 | 15 | 40 | 21.3 | 2.77 |  | 1580 | 15 | 80 | 21.3 | 3.73 |  | 8B | 8 | 13.7 | 2.3 | [6 empty] | 250 |  |  |  |  | 1.5 | 250 | 250 |  |  |  | 250 | 250
1580 | 15 | 80 | 21.3 | 3.73 |  | 205 | 20 | 5 | 26.7 | 1.65 |  | 10B | 10 | 17.1 | 2.3 | [6 empty] | 300 |  |  |  |  | 1.5 | 300 | 300 |  |  |  | 300 | 300
15160 | 15 | 160 | 21.3 | 4.78 |  | 2010 | 20 | 10 | 26.7 | 2.11 |  | 15B | 15 | 21.3 | 2.6 | [6 empty] | 350 |  |  |  |  | 1.5 | 350 | 350 |  |  |  | 350 | 350
205 | 20 | 5 | 26.7 | 1.65 |  | 2040 | 20 | 40 | 26.7 | 2.87 |  | 20B | 20 | 26.7 | 2.6 | [6 empty] | 400 |  |  |  |  | 1.5 | 400 | 400 |  |  |  | 400 | 400
2010 | 20 | 10 | 26.7 | 2.11 |  | 2080 | 20 | 80 | 26.7 | 3.91 |  | 25B | 25 | 33.4 | 3.2 | [6 empty] | 450 |  |  |  |  | 1.5 | 450 | 450 |  |  |  | 450 | 450
2030 | 20 | 30 | 26.7 | 2.41 |  | 255 | 25 | 5 | 33.4 | 1.65 |  | 32B | 32 | 42.16 | 3.2 | [6 empty] | 500 |  |  |  |  | 1.5 | 500 | 500 |  |  |  | 500 | 500
[22 empty] | 550 |  |  |  |  | 1.5 | 550 | 550
2040 | 20 | 40 | 26.7 | 2.87 |  | 2510 | 25 | 10 | 33.4 | 2.77 |  | 40B | 40 | 48.26 | 3.2 | [6 empty] | 600 |  |  |  |  | 1.5 | 600 | 600 |  |  |  | 550 | 550
2080 | 20 | 80 | 26.7 | 3.91 |  | 2540 | 25 | 40 | 33.4 | 3.38 |  | 50B | 50 | 60.3 | 3.6 | [6 empty] | 700 |  |  |  |  | 1.5 | 650 | 650 |  |  |  | 600 | 600
[22 empty] | 750 |  |  |  |  | 1.5 | 700 | 700
20160 | 20 | 160 | 26.7 | 5.56 |  | 2580 | 25 | 80 | 33.4 | 4.55 |  | 65B | 65 | 73.03 | 3.6 | [6 empty] | 800 |  |  |  |  | 1.5 | 750 | 750 |  |  |  | 750 | 750
255 | 25 | 5 | 33.4 | 1.65 |  | 325 | 32 | 5 | 42.2 | 1.65 |  | 80B | 80 | 88.9 | 4 | [6 empty] | 900 |  |  |  |  | 1.5 | 800 | 800
2510 | 25 | 10 | 33.4 | 2.77 |  | 3210 | 32 | 10 | 42.2 | 2.77 |  | 100B | 100 | 114.3 | 4.5 | [12 empty] | 850 | 850
2530 | 25 | 30 | 33.4 | 2.9 |  | 3240 | 32 | 40 | 42.2 | 3.56 |  | 125B | 125 | 141.3 | 4.8 | [12 empty] | 900 | 900
2540 | 25 | 40 | 33.4 | 3.38 |  | 3280 | 32 | 80 | 42.2 | 4.85 |  | 150B | 150 | 168.28 | 4.8
2580 | 25 | 80 | 33.4 | 4.55 |  | 405 | 40 | 5 | 48.3 | 1.65 |  |  | Carbon Steel IS 1239 : HEAVY
25160 | 25 | 160 | 33.4 | 6.35 |  | 4010 | 40 | 10 | 48.3 | 2.77 |  | C | Pipe Size (NB) | Outside Diameter(mm) | Wall Thickness(mm)
325 | 32 | 5 | 42.2 | 1.65 |  | 4040 | 40 | 40 | 48.3 | 3.68 |  | 6C | 6 | 10.3 | 2.6
3210 | 32 | 10 | 42.2 | 2.77 |  | 4080 | 40 | 80 | 48.3 | 5.08 |  | 8C | 8 | 13.7 | 2.9
3230 | 32 | 30 | 42.2 | 2.97 |  | 505 | 50 | 5 | 60.3 | 1.65 |  | 10C | 10 | 17.1 | 2.9
3240 | 32 | 40 | 42.2 | 3.56 |  | 5010 | 50 | 10 | 60.3 | 2.77 |  | 15C | 15 | 21.3 | 3.2
3280 | 32 | 80 | 42.2 | 4.85 |  | 5040 | 50 | 40 | 60.3 | 3.91 |  | 20C | 20 | 26.7 | 3.2
32160 | 32 | 160 | 42.2 | 6.35 |  | 5080 | 50 | 80 | 60.3 | 5.54 |  | 25C | 25 | 33.4 | 4
405 | 40 | 5 | 48.3 | 1.65 |  | 655 | 65 | 5 | 73 | 2.11 |  | 32C | 32 | 42.16 | 4
4010 | 40 | 10 | 48.3 | 2.77 |  | 6510 | 65 | 10 | 73 | 3.05 |  | 40C | 40 | 48.26 | 4
4030 | 40 | 30 | 48.3 | 3.18 |  | 6540 | 65 | 40 | 73 | 5.16 |  | 50C | 50 | 60.3 | 4.5
4040 | 40 | 40 | 48.3 | 3.68 |  | 6580 | 65 | 80 | 73 | 7.01 |  | 65C | 65 | 73.03 | 4.5
4080 | 40 | 80 | 48.3 | 5.08 |  | 805 | 80 | 5 | 88.9 | 2.11 |  | 80C | 80 | 88.9 | 4.8
40160 | 40 | 160 | 48.3 | 7.14 |  | 8010 | 80 | 10 | 88.9 | 3.05 |  | 100C | 100 | 114.3 | 5.4
505 | 50 | 5 | 60.3 | 1.65 |  | 8040 | 80 | 40 | 88.9 | 5.49 |  | 125C | 125 | 141.3 | 5.4
5010 | 50 | 10 | 60.3 | 2.77 |  | 8080 | 80 | 80 | 88.9 | 7.62 |  | 150C | 150 | 168.28 | 5.4
5030 | 50 | 30 | 60.3 | 3.18 |  | 905 | 90 | 5 | 101.6 | 2.11
5040 | 50 | 40 | 60.3 | 3.91 |  | 9010 | 90 | 10 | 101.6 | 3.05
5080 | 50 | 80 | 60.3 | 5.54 |  | 9040 | 90 | 40 | 101.6 | 5.74
50160 | 50 | 160 | 60.3 | 8.74 |  | 9080 | 90 | 80 | 101.6 | 8.08
655 | 65 | 5 | 73 | 2.11 |  | 1005 | 100 | 5 | 114.3 | 2.11
6510 | 65 | 10 | 73 | 3.05 |  | 10010 | 100 | 10 | 114.3 | 3.05
6530 | 65 | 30 | 73 | 4.78 |  | 10040 | 100 | 40 | 114.3 | 6.02
6540 | 65 | 40 | 73 | 5.16 |  | 10080 | 100 | 80 | 114.3 | 8.56
6580 | 65 | 80 | 73 | 7.01 |  | 1255 | 125 | 5 | 141.3 | 2.77
65160 | 65 | 160 | 73 | 9.53 |  | 12510 | 125 | 10 | 141.3 | 3.4
805 | 80 | 5 | 88.9 | 2.11 |  | 12540 | 125 | 40 | 141.3 | 6.55
8010 | 80 | 10 | 88.9 | 3.05 |  | 12580 | 125 | 80 | 141.3 | 9.53
8030 | 80 | 30 | 88.9 | 4.78 |  | 1505 | 150 | 5 | 168.3 | 2.77
8040 | 80 | 40 | 88.9 | 5.49 |  | 15010 | 150 | 10 | 168.3 | 3.4
8080 | 80 | 80 | 88.9 | 7.62 |  | 15040 | 150 | 40 | 168.3 | 7.11
80160 | 80 | 160 | 88.9 | 11.13 |  | 15080 | 150 | 80 | 168.3 | 10.97
1005 | 100 | 5 | 114.3 | 2.11 |  | 2005 | 200 | 5 | 219.1 | 2.77
10010 | 100 | 10 | 114.3 | 3.05 |  | 20010 | 200 | 10 | 219.1 | 3.76
10030 | 100 | 30 | 114.3 | 4.78 |  | 20040 | 200 | 40 | 219.1 | 8.18
10040 | 100 | 40 | 114.3 | 6.02 |  | 20080 | 200 | 80 | 219.1 | 12.7
10080 | 100 | 80 | 114.3 | 8.56 |  | 2505 | 250 | 5 | 273.1 | 3.4
100120 | 100 | 120 | 114.3 | 11.13 |  | 25010 | 250 | 10 | 273.1 | 4.19
100160 | 100 | 160 | 114.3 | 13.49 |  | 25040 | 250 | 40 | 273.1 | 9.27
1255 | 125 | 5 | 141.3 | 2.77 |  | 25080 | 250 | 80 | 273.1 | 12.7
12510 | 125 | 10 | 141.3 | 3.4 |  | 3005 | 300 | 5 | 323.9 | 3.96
12540 | 125 | 40 | 141.3 | 6.55 |  | 30010 | 300 | 10 | 323.9 | 4.57
12580 | 125 | 80 | 141.3 | 9.53 |  | 30040 | 300 | 40 | 323.9 | 9.53
125120 | 125 | 120 | 141.3 | 12.7 |  | 30080 | 300 | 80 | 323.9 | 12.7
125160 | 125 | 160 | 141.3 | 15.88 |  | 3505 | 350 | 5 | 355.6 | 3.96
1505 | 150 | 5 | 168.3 | 2.77 |  | 35010 | 350 | 10 | 355.6 | 4.78
15010 | 150 | 10 | 168.3 | 3.4 |  | 35040 | 350 | 40 | 355.6 | 9.53
15040 | 150 | 40 | 168.3 | 7.11 |  | 35080 | 350 | 80 | 355.6 | 12.7
15080 | 150 | 80 | 168.3 | 10.97 |  | 4005 | 400 | 5 | 406.4 | 4.19
150120 | 150 | 120 | 168.3 | 14.27 |  | 40010 | 400 | 10 | 406.4 | 4.78
150160 | 150 | 160 | 168.3 | 18.26 |  | 40040 | 400 | 40 | 406.4 | 9.53
2005 | 200 | 5 | 219.1 | 2.77 |  | 40080 | 400 | 80 | 406.4 | 12.7
20010 | 200 | 10 | 219.1 | 3.76 |  | 4505 | 450 | 5 | 457 | 4.19
20020 | 200 | 20 | 219.1 | 6.35 |  | 45010 | 450 | 10 | 457 | 4.78
20030 | 200 | 30 | 219.1 | 7.04 |  | 45040 | 450 | 40 | 457 | 9.53
20040 | 200 | 40 | 219.1 | 8.18 |  | 45080 | 450 | 80 | 457 | 12.7
20060 | 200 | 60 | 219.1 | 10.31 |  | 5005 | 500 | 5 | 508 | 4.78
20080 | 200 | 80 | 219.1 | 12.7 |  | 50010 | 500 | 10 | 508 | 5.54
200100 | 200 | 100 | 219.1 | 15.09 |  | 50040 | 500 | 40 | 508 | 9.53
200120 | 200 | 120 | 219.1 | 18.26 |  | 50080 | 500 | 80 | 508 | 12.7
200140 | 200 | 140 | 219.1 | 20.62 |  | 5505 | 550 | 5 | 559 | 4.78
200160 | 200 | 160 | 219.1 | 23.01 |  | 55010 | 550 | 10 | 559 | 5.54
2505 | 250 | 5 | 273 | 3.4 |  | 55040 | 550 | 40 | 559 | N/A
25010 | 250 | 10 | 273 | 4.19 |  | 55080 | 550 | 80 | 559 | N/A
25020 | 250 | 20 | 273 | 6.35 |  | 6005 | 600 | 5 | 610 | 5.54
25030 | 250 | 30 | 273 | 7.8 |  | 60010 | 600 | 10 | 610 | 6.35
25040 | 250 | 40 | 273 | 9.27 |  | 60040 | 600 | 40 | 610 | 9.53
25060 | 250 | 60 | 273 | 12.7 |  | 60080 | 600 | 80 | 610 | 12.7
25080 | 250 | 80 | 273 | 15.09 |  | 7505 | 750 | 5 | 762 | 6.35
250100 | 250 | 100 | 273 | 18.26 |  | 75010 | 750 | 10 | 762 | 7.92
250120 | 250 | 120 | 273 | 21.44 |  | 75040 | 750 | 40 | 762 | N/A
250140 | 250 | 140 | 273 | 25.4 |  | 75080 | 750 | 80 | 762 | N/A
250160 | 250 | 160 | 273 | 28.58
3005 | 300 | 5 | 323.8 | 3.96
30010 | 300 | 10 | 323.8 | 4.57
30020 | 300 | 20 | 323.8 | 6.35
30030 | 300 | 30 | 323.8 | 8.38
30040 | 300 | 40 | 323.8 | 10.31
30060 | 300 | 60 | 323.8 | 14.27
30080 | 300 | 80 | 323.8 | 17.48
300100 | 300 | 100 | 323.8 | 21.44
300120 | 300 | 120 | 323.8 | 25.4
300140 | 300 | 140 | 323.8 | 28.58
300160 | 300 | 160 | 323.8 | 33.32
3505 | 350 | 5 | 355.6 | 3.96
35010 | 350 | 10 | 355.6 | 6.35
35020 | 350 | 20 | 355.6 | 7.92
35030 | 350 | 30 | 355.6 | 9.53
35040 | 350 | 40 | 355.6 | 11.13
35060 | 350 | 60 | 355.6 | 15.09
35080 | 350 | 80 | 355.6 | 19.05
350100 | 350 | 100 | 355.6 | 23.83
350120 | 350 | 120 | 355.6 | 27.79
350140 | 350 | 140 | 355.6 | 31.75
350160 | 350 | 160 | 355.6 | 35.71
4005 | 400 | 5 | 406.4 | 4.19
40010 | 400 | 10 | 406.4 | 6.35
40020 | 400 | 20 | 406.4 | 7.92
40030 | 400 | 30 | 406.4 | 9.53
40040 | 400 | 40 | 406.4 | 12.7
40060 | 400 | 60 | 406.4 | 16.66
40080 | 400 | 80 | 406.4 | 21.44
400100 | 400 | 100 | 406.4 | 26.19
400120 | 400 | 120 | 406.4 | 30.96
400140 | 400 | 140 | 406.4 | 36.53
400160 | 400 | 160 | 406.4 | 40.49
4505 | 450 | 5 | 457 | 4.19
45010 | 450 | 10 | 457 | 6.35
45020 | 450 | 20 | 457 | 7.92
45030 | 450 | 30 | 457 | 11.13
45040 | 450 | 40 | 457 | 14.27
45060 | 450 | 60 | 457 | 19.05
45080 | 450 | 80 | 457 | 23.83
450100 | 450 | 100 | 457 | 29.36
450120 | 450 | 120 | 457 | 34.93
450140 | 450 | 140 | 457 | 39.67
450160 | 450 | 160 | 457 | 45.24
5005 | 500 | 5 | 508 | 4.78
50010 | 500 | 10 | 508 | 6.35
50020 | 500 | 20 | 508 | 9.53
50030 | 500 | 30 | 508 | 12.7
50040 | 500 | 40 | 508 | 15.09
50060 | 500 | 60 | 508 | 20.62
50080 | 500 | 80 | 508 | 26.19
500100 | 500 | 100 | 508 | 32.54
500120 | 500 | 120 | 508 | 38.1
500140 | 500 | 140 | 508 | 44.45
500160 | 500 | 160 | 508 | 50.01
5505 | 550 | 5 | 559 | 4.78
55010 | 550 | 10 | 559 | 6.35
55020 | 550 | 20 | 559 | 9.53
55030 | 550 | 30 | 559 | 12.7
55060 | 550 | 60 | 559 | 22.23
55080 | 550 | 80 | 559 | 28.58
550100 | 550 | 100 | 559 | 34.93
550120 | 550 | 120 | 559 | 41.28
550140 | 550 | 140 | 559 | 47.63
550160 | 550 | 160 | 559 | 53.98
6005 | 600 | 5 | 610 | 5.54
60010 | 600 | 10 | 610 | 6.35
60020 | 600 | 20 | 610 | 9.53
60030 | 600 | 30 | 610 | 14.27
60040 | 600 | 40 | 610 | 17.48
60060 | 600 | 60 | 610 | 24.61
60080 | 600 | 80 | 610 | 30.96
600100 | 600 | 100 | 610 | 38.89
600120 | 600 | 120 | 610 | 46.02
600140 | 600 | 140 | 610 | 52.37
600160 | 600 | 160 | 610 | 59.54
65010 | 650 | 10 | 660 | 7.92
65020 | 650 | 20 | 660 | 12.7
70010 | 700 | 10 | 711 | 7.92
70020 | 700 | 20 | 711 | 12.7
70030 | 700 | 30 | 711 | 15.88
7505 | 750 | 5 | 762 | 6.35
75010 | 750 | 10 | 762 | 7.92
75020 | 750 | 20 | 762 | 12.7
75030 | 750 | 30 | 762 | 15.88
80010 | 800 | 10 | 813 | 7.92
80020 | 800 | 20 | 813 | 12.7
80030 | 800 | 30 | 813 | 15.88
80040 | 800 | 40 | 813 | 17.48
85010 | 850 | 10 | 864 | 7.92
85020 | 850 | 20 | 864 | 12.7
85030 | 850 | 30 | 864 | 15.88
85040 | 850 | 40 | 864 | 17.48
90010 | 900 | 10 | 914 | 7.92
90020 | 900 | 20 | 914 | 12.7
90030 | 900 | 30 | 914 | 15.88
90040 | 900 | 40 | 914 | 19.05
| Nominal pipe size |  | Outside Dia | Nominl wall thickness schedule
| NPS | DN | OD | 5S | 10S | 10 | 20 | 30 | 40S | STD | 40 | 60 | 80S | XS | 80 | 100 | 120 | 140 | 160 | XXS
| 2025-01-08 | 6 | 10.3 |  | 1.24 |  |  |  | 1.73 | 1.73 | 1.73 |  | 2.41 | 2.41 | 2.41 | [6 empty] | A335P11
| 2025-01-04 | 8 | 13.7 |  | 1.65 |  |  |  | 2.24 | 2.24 | 2.24 |  | 3.02 | 3.02 | 3.02 | [6 empty] | 6 | A335P116 | 5 | 10 | 40 | 80
| 2025-03-08 | 10 | 17.1 |  | 1.65 |  |  |  | 2.31 | 2.31 | 2.31 |  | 3.2 | 3.2 | 3.2 | [6 empty] | 8 | A335P118 | 5 | 10 | 40 | 80
| 2025-01-02 | 15 | 21.3 | 1.65 | 2.11 |  |  |  | 2.77 | 2.77 | 2.77 |  | 3.73 | 3.73 | 3.73 |  |  |  | 4.78 | 7.47 |  | 10 | 810 | 5 | 10 | 40 | 80
| 2025-03-04 | 20 | 26.9 | 1.65 | 2.11 |  |  |  | 2.87 | 2.87 | 2.87 |  | 3.91 | 3.91 | 3.91 |  |  |  | 5.56 | 7.82 |  | 15 | 1015 | 5 | 10 | 40 | 80
| 1 | 25 | 33.7 | 1.65 | 2.77 |  |  |  | 3.38 | 3.38 | 3.38 |  | 4.55 | 4.55 | 4.55 |  |  |  | 6.35 | 9.09 |  | 20 | 1520 | 5 | 10 | 40 | 80
| 1 1/4 | 32 | 42.4 | 1.65 | 2.77 |  |  |  | 3.56 | 3.56 | 3.56 |  | 4.85 | 4.85 | 4.85 |  |  |  | 6.35 | 9.7 |  | 25 | 2025 | 5 | 10 | 40 | 80
| 1 1/2 | 40 | 48.3 | 1.65 | 2.77 |  |  |  | 3.68 | 3.68 | 3.68 |  | 5.08 | 5.08 | 5.08 |  |  |  | 7.14 | 10.15 |  | 32 | 2532 | 5 | 10 | 40 | 80
| 2 | 50 | 60.3 | 1.65 | 2.77 |  |  |  | 3.91 | 3.91 | 3.91 |  | 5.54 | 5.54 | 5.54 |  |  |  | 8.74 | 11.07 |  | 40 | 3240 | 5 | 10 | 40 | 80
| 2 1/2 | 65 | 73 | 2.11 | 3.05 |  |  |  | 5.16 | 5.16 | 5.16 |  | 7.01 | 7.01 | 7.01 |  |  |  | 9.53 | 14.02 |  | 50 | 4050 | 5 | 10 | 40 | 80
| 3 | 80 | 88.9 | 2.11 | 3.05 |  |  |  | 5.49 | 5.49 | 5.49 |  | 7.62 | 7.62 | 7.62 |  |  |  | 11.13 | 15.24 |  | 65 | 5065 | 5 | 10 | 40 | 80
| 3 1/2 | 90 | 101.6 | 2.11 | 3.05 |  |  |  | 5.74 | 5.74 | 5.74 |  | 8.08 | 8.08 | 8.08 | [6 empty] | 80 | 6580 | 5 | 10 | 40 | 80
| 4 | 100 | 114.3 | 2.11 | 3.05 |  |  |  | 6.02 | 6.02 | 6.02 |  | 8.56 | 8.56 | 8.56 |  |  |  | 13.49 | 17.12 |  | 100 | 80100 | 5 | 10 | 40 | 80
| 5 | 125 | 141.3 | 2.77 | 3.4 |  |  |  | 6.55 | 6.55 | 6.55 |  | 9.53 | 9.53 | 9.53 |  |  |  | 15.88 | 19.05 |  | 125 | 100125 | 5 | 10 | 40 | 80
| 6 | 150 | 168.3 | 2.77 | 3.4 |  |  |  | 7.11 | 7.11 | 7.11 |  | 10.97 | 10.97 | 10.97 |  |  |  | 18.26 | 21.95 |  | 150 | 125150 | 5 | 10 | 40 | 80
| 8 | 200 | 219.1 | 2.77 | 3.76 |  | 6.35 | 7.04 | 8.18 | 8.18 | 8.18 | 10.31 | 12.7 | 12.7 | 12.7 | 15.09 |  |  | 23.01 | 22.23 |  | 200 | 150200 | 5 | 10 | 40 | 80
| 10 | 250 | 273.1 | 3.4 | 4.19 |  | 6.35 | 7.8 | 9.27 | 9.27 | 9.27 | 12.7 | 12.7 | 12.7 | 15.09 | 18.26 |  |  | 28.58 | 25.4 |  | 250 | 200250 | 5 | 10 | 40 | 80
| 12 | 300 | 323.9 | 3.96 | 4.57 |  | 6.35 | 8.38 | 9.53 | 9.53 | 10.31 | 14.27 | 12.7 | 12.7 | 17.48 | 21.44 |  |  | 33.32 | 25.4 |  | 300 | 250300 | 5 | 10 | 40 | 80
| 14 | 350 | 355.6 | 3.96 | 4.78 | 6.35 | 7.92 | 9.53 |  | 9.53 | 11.13 | 15.09 |  | 12.7 | 19.05 | 23.83 |  |  | 35.71 |  |  | 350 | 300350 | 5 | 10 | 40 | 80
| 16 | 400 | 406.4 | 4.19 | 4.78 | 6.35 | 7.92 | 9.53 |  | 9.53 | 12.7 | 16.66 |  | 12.7 | 21.44 | 26.19 |  |  | 40.49 |  |  | 400 | 350400 | 5 | 10 | 40 | 80
| 18 | 450 | 457 | 4.19 | 4.78 | 6.35 | 7.92 | 11.13 |  | 9.53 | 14.27 | 19.05 |  | 12.7 | 23.83 | 29.36 |  |  | 45.24 |  |  | 450 | 400450 | 5 | 10 | 40 | 80
| 20 | 500 | 508 | 4.78 | 5.54 | 6.35 | 9.53 | 12.7 |  | 9.53 | 15.09 | 20.62 |  | 12.7 | 26.19 | 32.54 |  |  | 50.01 |  |  | 500 | 450500 | 5 | 10 | 40 | 80
| 22 |  | 559 | 4.78 | 5.54 | 6.35 | 9.53 | 12.7 |  | 9.53 |  | 22.23 |  | 12.7 | 28.58 | 34.93 |  |  | 53.98 |  |  | 550 | 500550 | 5 | 10 | 40 | 80
| 24 | 600 | 610 | 5.54 | 6.35 | 6.35 | 9.53 | 14.27 |  | 9.53 | 17.48 | 24.61 |  | 12.7 | 30.96 | 38.89 |  |  | 59.54 |  |  | 600 | 550600 | 5 | 10 | 40 | 80
| 26 |  | 660 |  |  | 7.92 | 12.7 |  |  | 9.53 |  |  |  | 12.7 | [7 empty] | 750 | 600750 | 5 | 10 | 40 | 80
| 28 | 700 | 711 |  |  | 7.92 | 12.7 | 15.88 |  | 9.53 |  |  |  | 12.7
| 30 |  | 762 | 6.35 | 7.92 | 7.92 | 12.7 | 15.88 |  | 9.53 |  |  |  | 12.7 | [7 empty] | A335P22
| 32 | 800 | 813 |  |  | 7.92 | 12.7 | 15.88 |  | 9.53 |  |  |  | 12.7 | [7 empty] | 6 | A335P226 | 5 | 10 | 40 | 80
| 34 |  | 884 |  |  | 7.92 | 12.7 | 15.88 |  | 9.53 |  |  |  | 12.7 | [7 empty] | 8 | 68 | 5 | 10 | 40 | 80
| 36 | 900 | 914 |  |  | 7.92 | 12.7 | 15.88 |  | 9.53 |  |  |  | 12.7 | [7 empty] | 10 | 10 | 5 | 10 | 40 | 80
| 38 |  | 965 | [6 empty] | 9.53 |  |  |  | 12.7 | [7 empty] | 15 | 15 | 5 | 10 | 40 | 80
| 40 | 1000 | 1016 | [18 empty] | 20 | 20 | 5 | 10 | 40 | 80
|  | 1067 | [5 empty] | 15.88 | [13 empty] | 25 | 25 | 5 | 10 | 40 | 80

## 16 PRS Steam Saving
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
Steam Saving in PRS
Data to be Entered |  |  | INDEX | Data to be Genreted
Input Pressure | 10 | bar |  | Latent Heat at Inlet Pressure | 477.35 | kcal/kg
Out Pressure | 6 | bar |  | Latent Heat at Outlet Pressure | 493.39 | kcal/kg
Flow Rate | 2700 | kg/hr |  |  | 16.04 | kcal/kg
Data to be Calculate
Energy required without prs | 1288845 | kcal/hr
Energy will be Genrate with PRS | 1332153 | kcal/hr |  | Steam Flowrate required after the installation of PRS is | 2612.2236 | kg/hr
Steam flow rate required(with prs) | 2612.2236 | kg/hr |  | So total saving of steam is | 87.7764 | kg/hr
Steam Flowrate required after the instaletion of PRS is 2612.2235959383 so total saving of steam is 87.7764040616958

## Sheet 17 Superheated Steam Cal
VOLFRAM SYSTEMS INDIA PVT. LTD.
www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
ONLY SUPERHEATED STEAM PIPE SIZE CALCULATOR
Calculation of Pipe Diameter from Steam Flow |  |  |  | REFERANCE- AE for myChemEngmusings.Wordpress.com
Steam Pressure | 1.5 | bar | 647.14 |  |  |  | Percentage Error Calculation
Steam Temperature | 359 | celsius | 220.64 | Enthalpy=1892+4.52*Zpbe_H2O*R*T/MW |  |  | Pressure | Temperature | Enthalpy as per TLV | Enthalpy as per calculator | % error
Steam Flow rate | 40000 | kg/hr |  |  |  |  | 2 | 150 | 661.512 | 659.52 | 0.3%
Steam Velocity | 35 | m/sec |  | Density=P*100*MW/Zpbe_H2O*R*T |  |  | 2 | 160 | 666.427 | 664.78 | 0.25%
[7 empty] | 2 | 170 | 671.306 | 670.026 | 0.19%
Steam temp | 632.14 | kelvin |  | Zpbe_H2O=1-(0.3411*Pr)/Tr^4.111*(1-0.3411*Pr/Tr^4.111) |  |  | 2 | 180 | 676.157 | 675.24 | 0.14%
Temp reduction | 0.97682 | [5 empty] | 2 | 190 | 680.988 | 680.43 | 0.08%
Pressure reduction | 0.0067984 | [5 empty] | 2 | 200 | 685.805 | 685.611 | 0.03%
Zpbe_H2O | 0.99744 |  |  | Symbol | Description | Unit | 2 | 210 | 690.612 | 690.77 | -0.02%
[7 empty] | 2 | 260 | 714.613 | 716.38 | -0.25%
Enthalpy | 3208.3638 | KJ/Kg |  |  |  |  | 2 | 270 | 719.422 | 721.48 | -0.29%
Enthalpy | 766.8173 | Kcal/Kg |  | T | Superheat Temperature | kelvin | 2 | 300 | 733.895 | 736.72 | -0.38%
Density | 0.51506 | Kg/m3 |  | P | Steam Pressure | Bar | 2 | 350 | 758.216 | 762.007 | -0.5%
Specific volume | 1.9415 | m3/kg |  | Zpbe | Compressibility factor of superheated steam
Diameter of pipe | 0.88588 | m |  | MW | Molecular weight of water (18) | g/mol | 5 | 160 | 661.103 | 659.258 | 0.28%
Diameter of Pipe | 885.8759 | mm |  | R | Universl gas constant (8.314) | KJ/KmolK | 5 | 170 | 666.552 | 664.9 | 0.25%
|  |  |  | Tr | Temperature reduction (T/Tc) |  | 5 | 180 | 671.871 | 670.48 | 0.21%
|  |  |  | Pr | Pressure redection (P/Pc) |  | 5 | 190 | 677.096 | 676.007 | 0.16%
|  |  |  | Tc | Critical Temperature (647.14) | Kelvin | 5 | 200 | 682.249 | 681.48 | 0.11%
|  |  |  | Pc | Critical Pressure (220.64) | Bar | 5 | 210 | 687.348 | 686.91 | 0.06%
[7 empty] | 5 | 250 | 707.389 | 708.306 | -0.13%
[7 empty] | 5 | 260 | 712.347 | 713.58 | -0.17%
[7 empty] | 5 | 300 | 732.106 | 734.49 | -0.33%
[7 empty] | 5 | 350 | 756.823 | 760.3 | -0.46%
[7 empty] | 10 | 180 | 663.505 | 662.09 | 0.21%
[7 empty] | 10 | 190 | 669.737 | 668.24 | 0.22%
[7 empty] | 10 | 200 | 675.649 | 674.24 | 0.21%
[7 empty] | 10 | 210 | 681.367 | 680.21 | 0.17%
[7 empty] | 10 | 220 | 686.945 | 686.062 | 0.13%
[7 empty] | 10 | 250 | 703.111 | 703.18 | -0.01%
[7 empty] | 10 | 300 | 729.026 | 730.71 | -0.23%
[7 empty] | 10 | 350 | 754.459 | 757.41 | -0.39%
[7 empty] | 20 | 220 | 674.074 | 672.58 | 0.22%
[7 empty] | 20 | 230 | 680.881 | 679.328 | 0.23%
[7 empty] | 20 | 240 | 687.341 | 685.904 | 0.21%
[7 empty] | 20 | 250 | 693.557 | 692.335 | 0.18%
[7 empty] | 20 | 300 | 722.468 | 722.835 | -0.05%
[7 empty] | 20 | 350 | 749.556 | 751.484 | -0.26%
[7 empty] | 50 | 270 | 673.636 | 672.038 | 0.24%
[7 empty] | 50 | 280 | 682.77 | 680.5029 | 0.33%
[7 empty] | 50 | 290 | 691.114 | 688.626 | 0.36%
[7 empty] | 50 | 300 | 698.912 | 696.453 | 0.35%
[7 empty] | 50 | 350 | 733.228 | 732.273 | 0.13%
[7 empty] | 100 | 350 | 698.509 | 694.61 | 0.56%
[7 empty] | 100 | 400 | 739.937 | 737.23 | 0.37%
[7 empty] | 100 | 450 | 774.553 | 773.85 | 0.09%

## Class
| A106 Gr. B150 | 5 | 10 | 40 | 80 | 120 | 160 | [7 empty] | INDEX
A516 Gr. 70
250 | A516 Gr. 70250 | 5 | 6 | 8 | 10 | 12 | 15 | 16 | 20 | 25 | 32 | 40 | 50 | 60
300 | A516 Gr. 70300 | 5 | 6 | 8 | 10 | 12 | 15 | 16 | 20 | 25 | 32 | 40 | 50 | 60
350 | A516 Gr. 70350 | 5 | 6 | 8 | 10 | 12 | 15 | 16 | 20 | 25 | 32 | 40 | 50 | 60
400 | A516 Gr. 70400 | 5 | 6 | 8 | 10 | 12 | 15 | 16 | 20 | 25 | 32 | 40 | 50 | 60
450 | A516 Gr. 70450 | 5 | 6 | 8 | 10 | 12 | 15 | 16 | 20 | 25 | 32 | 40 | 50 | 60
500 | A516 Gr. 70500 | 5 | 6 | 8 | 10 | 12 | 15 | 16 | 20 | 25 | 32 | 40 | 50 | 60
600 | A516 Gr. 70600 | 5 | 6 | 8 | 10 | 12 | 15 | 16 | 20 | 25 | 32 | 40 | 50 | 60
700 | A516 Gr. 70700 | 5 | 6 | 8 | 10 | 12 | 15 | 16 | 20 | 25 | 32 | 40 | 50 | 60
800 | A516 Gr. 70800 | 5 | 6 | 8 | 10 | 12 | 15 | 16 | 20 | 25 | 32 | 40 | 50 | 60
900 | A516 Gr. 70900 | 5 | 6 | 8 | 10 | 12 | 15 | 16 | 20 | 25 | 32 | 40 | 50 | 60
A106 Gr. B
6 | A106 Gr. B6 | 10 | 30 | 40 | 80
8 | A106 Gr. B8 | 10 | 30 | 40 | 80
10 | A106 Gr. B10 | 10 | 30 | 40 | 80
15 | A106 Gr. B15 | 5 | 10 | 30 | 40 | 80 | 160
20 | A106 Gr. B20 | 5 | 10 | 30 | 40 | 80 | 160
25 | A106 Gr. B25 | 5 | 10 | 30 | 40 | 80 | 160
32 | A106 Gr. B32 | 5 | 10 | 30 | 40 | 80 | 160
40 | A106 Gr. B40 | 5 | 10 | 30 | 40 | 80 | 160
50 | A106 Gr. B50 | 5 | 10 | 30 | 40 | 80 | 160
65 | A106 Gr. B65 | 5 | 10 | 30 | 40 | 80 | 160
80 | A106 Gr. B80 | 5 | 10 | 30 | 40 | 80 | 160
100 | A106 Gr. B100 | 5 | 10 | 30 | 40 | 80 | 120 | 160
125 | A106 Gr. B125 | 5 | 10 | 40 | 80 | 120 | 160
150 | A106 Gr. B150 | 5 | 10 | 40 | 80 | 120 | 160
200 | A106 Gr. B200 | 5 | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160
250 | A106 Gr. B250 | 5 | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160
300 | A106 Gr. B300 | 5 | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160
IS1239
6 | IS12396 | A | B | C
8 | IS12398 | A | B | C
10 | IS123910 | A | B | C
15 | IS123915 | A | B | C
20 | IS123920 | A | B | C
25 | IS123925 | A | B | C
32 | IS123932 | A | B | C
40 | IS123940 | A | B | C
50 | IS123950 | A | B | C
65 | IS123965 | A | B | C
80 | IS123980 | A | B | C
100 | IS1239100 | A | B | C
125 | IS1239125 | B | C
150 | IS1239150 | B | C
IS3589
150 | IS3589150 | 2.6 | 3.2 | 4 | 4.5
200 | IS3589200 | 2.6 | 3.6 | 4.5 | 6.3
250 | IS3589250 | 3.6 | 4 | 5 | 6.3
300 | IS3589300 | 4 | 4.5 | 5.6 | 7.1
350 | IS3589350 | 4 | 5 | 5.6 | 8
400 | IS3589400 | 4 | 5 | 6.3 | 8.8
450 | IS3589450 | 4 | 5 | 6.3 | 10
500 | IS3589500 | 5 | 5.6 | 6.3 | 11
600 | IS3589600 | 5.8 | 6.3 | 12.5
700 | IS3589700 | 6.3 | 7.1 | 14.2
800 | IS3589800 | 7.1 | 8 | 18
900 | IS3589900 | 8 | 8.8 | 10 | 17.5
SS304
6 | SS3046 | 5 | 10 | 40 | 80
8 | SS3048 | 5 | 10 | 40 | 80
10 | SS30410 | 5 | 10 | 40 | 80
15 | SS30415 | 5 | 10 | 40 | 80
20 | SS30420 | 5 | 10 | 40 | 80
25 | SS30425 | 5 | 10 | 40 | 80
32 | SS30432 | 5 | 10 | 40 | 80
40 | SS30440 | 5 | 10 | 40 | 80
50 | SS30450 | 5 | 10 | 40 | 80
65 | SS30465 | 5 | 10 | 40 | 80
80 | SS30480 | 5 | 10 | 40 | 80
100 | SS304100 | 5 | 10 | 40 | 80
125 | SS304125 | 5 | 10 | 40 | 80
150 | SS304150 | 5 | 10 | 40 | 80
200 | SS304200 | 5 | 10 | 40 | 80
250 | SS304250 | 5 | 10 | 40 | 80
300 | SS304300 | 5 | 10 | 40 | 80
350 | SS304350 | 5 | 10 | 40 | 80
400 | SS304400 | 5 | 10 | 40 | 80
450 | SS304450 | 5 | 10 | 40 | 80
500 | SS304500 | 5 | 10 | 40 | 80
550 | SS304550 | 5 | 10 | 40 | 80
600 | SS304600 | 5 | 10 | 40 | 80
750 | SS304750 | 5 | 10 | 40 | 80
SS316
6 | SS3166 | 5 | 10 | 40 | 80
8 | SS3168 | 5 | 10 | 40 | 80
10 | SS31610 | 5 | 10 | 40 | 80
15 | SS31615 | 5 | 10 | 40 | 80
20 | SS31620 | 5 | 10 | 40 | 80
25 | SS31625 | 5 | 10 | 40 | 80
32 | SS31632 | 5 | 10 | 40 | 80
40 | SS31640 | 5 | 10 | 40 | 80
50 | SS31650 | 5 | 10 | 40 | 80
65 | SS31665 | 5 | 10 | 40 | 80
80 | SS31680 | 5 | 10 | 40 | 80
100 | SS316100 | 5 | 10 | 40 | 80
125 | SS316125 | 5 | 10 | 40 | 80
150 | SS316150 | 5 | 10 | 40 | 80
200 | SS316200 | 5 | 10 | 40 | 80
250 | SS316250 | 5 | 10 | 40 | 80
300 | SS316300 | 5 | 10 | 40 | 80
350 | SS316350 | 5 | 10 | 40 | 80
400 | SS316400 | 5 | 10 | 40 | 80
450 | SS316450 | 5 | 10 | 40 | 80
500 | SS316500 | 5 | 10 | 40 | 80
550 | SS316550 | 5 | 10 | 40 | 80
600 | SS316600 | 5 | 10 | 40 | 80
750 | SS316750 | 5 | 10 | 40 | 80
MOC | CLASS/SCHEDULE
SS 304 | FL 150
SS 316 | FL 300
MS | FL 600
CI | FL 900
A216 WCB | FL 1500
CS | SW #800
A 216 WCC | SW #3000
SS 316L | BSP #150
A351 CF8 | BSP #300
A351 CF8M | NPT #800
A743 GR CA 40 | BSP #800
A106 Grade B | BUTT WELD #800
A 105 | NTP #3000
A 516 Grade 70 | BSP #3000
A234 WPB | PN 40
A193 | PN10
A194 | BUTT WELD #3000
Forged Cast steel | Tri clover A
IS 2062 | Tri clover B
A182 Gr. F11 | Tri clover C
A335 Gr. P11 | PN16
A335 Gr. P22 | NPT #600
A182 Gr. P22 | BSP #600
A217 Gr. WC 9 | SW #600
A217 Gr. WC 6 | BSP
A182 Gr. F22 | NPT
Butt Weld
SCHEDULE 5
SCHEDULE 10
SCHEDULE 20
SCHEDULE 40
SCHEDULE 80
SCHEDULE 120
SCHEDULE 160

## 18 PIPE THICKNESS P11 P22
VOLFRAM SYSTEMS INDIA PVT. LTD www.volfram.in ¦ steam@volfram.in ¦ +91 8378964757
PIPE WALL THICKNESS CALCULATOR ASME B31.3 |  |  | CALCULATIONS | [5 empty] | A335 P11 | A335 P22
[8 empty] | Temperature(°C) | Allowable Stress (Mpa) | Allowable Stress (Mpa)
|  |  | Symbol | Description | Value | Unit | Remark | 40 | 138 | 138
Pipe Type | Seamless |  | P | Operating Pressure | 9 | Mpa | Internal Design Pressure | 65 | 131 | 132
Material of Construction | Alloy steel |  | D | Outside Diameter of Pipe | 73 | mm | From ASME B36.10 | 100 | 126 | 128
Grade of Material | A335 P22 |  | S | Allowable Stress | 80.9 | Mpa | ASME B31.3-2016 Table A-1M | 125 | 124 | 126
Internal design Pressure(g) | 90 | bar | E | Quality Factor | 1 |  | ASME B31.3-2016 Tble (A 1-B) Basic Quality factor | 150 | 121 | 125
Operating Temperature | 500 | °C | W | Strength Reduction Factor | 1 |  | ASME Boiler and Pressure Vessel Code (BPVC), ASME B31.3, or ASME B31.1 | 175 | 119 | 124
Size of Pipe | 65 | NB | Y | Coefficient Y | 0.4 |  |  | 200 | 116 | 124
Schedule of Pipe / Class / Wall Thicknesses | 160 |  | t | Calculated Wall Thickness | 3.888 | mm |  | 225 | 115 | 124
Mechanical Allowance | 3 | mm | d1 | Major Diameter of Threading |  | mm |  | 250 | 113 | 124
|  |  | d2 | Minor Diameter of Threading |  | mm |  | 275 | 111 | 124
Minimum Required Thickness (tm) | 6.888 | mm | C | Sum of Mechanical Allowance | 3 | mm |  | 300 | 109 | 124
Actual Pipe Wall Thickness | 9.53 | mm | tm | Minimum Required Thickness (t+c) | 6.888 | mm |  | 325 | 107 | 124
DESIGN IS SAFE |  |  | T | Actual Pipe Wall Thickness | 9.53 | mm |  | 350 | 106 | 124
[8 empty] | 375 | 104 | 124
| SAFE | [6 empty] | 400 | 102 | 123
| NOT SAFE | [6 empty] | 425 | 99.6 | 122
[8 empty] | 450 | 97.2 | 121
[8 empty] | 475 | 94.5 | 99.6
[8 empty] | 500 | 73.5 | 80.9
[8 empty] | 525 | 52 | 63.3
[8 empty] | 550 | 36.3 | 47.5
[8 empty] | 575 | 25.2 | 34.2
[8 empty] | 600 | 17.6 | 23.5
[8 empty] | 625 | 12.3 | 15.3
[8 empty] | 650 | 8.27 | 9.65